## Charts (hidden)
Low | Moderate | Significant | High
#REF! | #REF! | #REF! | #REF!
| Backlog Year 0 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
Condition | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Statutory | #REF!

## Condition
#REF!
#REF! |  |  |  | Physical Condition
Site | Building | Level | Block No/Area/Dept | Main Element | Sub-Element | Rank A-D | Element Projected Remaining Life | Probability of Failure | Potential Consequences | Risk Score | Risk Ranking | Current Faults / Comments / Defects If below condition B | Remedial Action | Repair Quantity | Unit (m²/m/no.) | Rate | Net - Cost | Total Cost incl. Uplift | Cost to B | Impending Backlog |  |  |  |  | Future Capital Costs |  |  |  |  | Backlog Risk Costs
[20 empty] | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Low | Moderate | Significant | High
Hemel Hempstead Hospital | Site | Site | Site | External Works | External Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Underground external drainage system is reportedly aged and problematic at best. Some potential areas of collapsed drains reported. | Replace original site drainage system. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Roads / Parking Areas | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Worn and defective tarmac road surfaces evident across the site. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Paths | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Wear and tear evident to flag stone paths. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Paths | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some tarmac paths are aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Car Parks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Tarmac surfaces to majority of car parks is in poor condition. Damages surfaces and potholes evident to the majority. | Resurface affected areas. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some aged site fencing noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Barrier Entry & Exit Systems | B |  |  |  | 0 |  | Appear to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Signage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Street Furniture | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor to external handrails is aged and in poor condition. | Redecoration is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Street Furniture | B | 7 |  |  | 0 |  | Minimal defects noted. | Also required in the long term. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | External Works | Ancillary Buildings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Fuel Supply / Storage / Distribution | B | 8 |  |  | 0 |  | Minimal defects noted to site gas main. Circa 1990's. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Steam & Condensate Systems | Cx | 0 | Certain (5) | Major (4) | 20 | High | Steam main for district heating system is aged and problematic. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Hot & Cold Water Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Site water mains in some areas is aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Heating Systems | N/A |  |  |  | 0 |  | Refer to comments above under "Steam & Condensate System". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Chilled Water / Refrigeration Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Medical and Industrial Gases | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Air Tube Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Mechanical Systems | Service Subways / Ducts | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged HV Transformer 500kva remains in situ beyond intended design life. | Relace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged HV Transformer 800kva remains in situ beyond intended design life. | Relace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged HV Ring Main Units remain in situ beyond intended design life. | Relace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged HV cabling remains in situ beyond intended design life. | Relace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged back up generator remains in situ beyond intended design life. 406kva. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged back up generator remains in situ beyond intended design life. 800kva. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Electrical | Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some newer LED fittings noted, however, a large number of site lights are aged and due replacement. | Replace aged site lighting. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Communications | Telephone & Data Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Communications | Building Management systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Alarm Systems | Fire Alarm Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Security | CCTV Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Medical Gas Pipeline Services | Vacuum Insulated Evaporator | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Site | Site | Site | Miscellaneous | External Plant and Equipment | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Damage noted to the external tin profile cladding of the building. | Carry out necessary repairs. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cracking noted to external render. | Carry out repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Windows | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Leaf External Timber doors appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Leaf External Timber door appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External roller shutter door appears aged and passed intended design life; Signs of corrosion evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External render appears aged; lifecycle wear & tear is evident. | Repaint external render following repair works. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Fabric | Decoration | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Aluminium louvre panels appear aged; Signs of wear & tear evident from the external elements are evident. | Repaint external aluminium louvres. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Tin profile pitched roof appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Roof | Roof Lights | B |  |  |  | 0 |  | Perspex profile roof lights appear in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aluminium box guttering and downpipes appear aged. There is evidence of damage to downpipes from being struck; securing brackets were also noted to be bent and there was signs of leaking at some joints. | Replace damaged rain water guttering and downpipes. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer To Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fuel oil storage tank appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fuel / Oil pipework between storage tank and each boiler appears aged and passed intended design life. Leaks evident on all pipework. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No. Fuel / Oil transfer pumps appear aged and passed intended design life. Leaks evident on all pipework. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  | Gas supply pipework appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Major (4) | 20 | High | 3No. Dual Fuel (gas/oil) fired steam boilers (circa 1998) including associated bespoke LV and Control Panels appear aged and passed intended design life. Leaks noted on each boiler. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No. (Twin) Steam Calorifiers appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No. Condensate Receiver Vessel & associated Pumps appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Flues - Separate | Cx | 0 | Certain (5) | Major (4) | 20 | High | Flue headers (including modulating dampers - operational status unknown) and external 25m high , stand alone, steel flues appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Control panel (In Hotwell Tank Rm.) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Control panel (In Calorifier Plant Rm.) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No. Steam Blow Down Vessel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No. Hotwell / Softened Water Make-up Tank appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No. Condensate Return Header Vessel (circa Nov. 1996) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No. Sludge Collection Vessel (circa Nov. 1996) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | All Steam; Condense & Heating Pipework throughout the boiler house appears aged and passed intended design life. Various leaks evident at time of survey. | Replace all necessary pipework. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating Systems | Heating Pumps | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | 2No. LPHW Pumps appear aged and approaching the end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating Systems | Heating Pumps | B(C) | 1 | Likely (4) | Major (4) | 16 | Significant | 3No. Primary Circulation Pumps (1 on each boiler) appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Water Softening Unit appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 2No. Water Treatment Plant (chemical dosing units); appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV Main Switch Panel (In Boiler Rm Office) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV Main Switch Panel (In Calorifier Rm.) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No. Floodlight / Photocell appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | BMS System appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Industrial Gas Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls in the Hotwell room. | Carry out repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted concrete floors are aged. Lifecycle wear & tear evident. | Repaint floors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Leaf Internal Timber doors appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | White-Washed Brick / Block walls have evidence of lifecycle wear & tear. | Repaint the walls. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration anticipated. | Long term lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | All heating pipework appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (Hagar - plastic enclosure) distribution board appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (Merlin Gerin) distribution board appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | There is evidence of newer LED light fittings; However, some old fluorescent light fittings remain in situ that appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Gas leak detection alarms appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Boiler House | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Structure | Foundations | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cheere House is currently boarded up and not in use. Building appears to be falling into disrepair and requires a complete refurbishment if it is to be brought back in to use. | Full refurbishment is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Structure | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Structure | Frames | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Structure | Floors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Structure | Roofs | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Windows | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Roof | Rain Water Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Luminaires External | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Cheere House | All | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Spalling and damage noted to areas of brick work and the around the flat roof parapet. Also, brickwork to workshop 001 has cracked due to possible subsidence. | Recommend a structural survey of the brickwork / walls. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Damage to brickwork and mortar as well as spalling noted to various areas around the building. | Budget cost for repairs to various areas of damaged brick walls and repointing works where required. *NOTE - Budget may need to increase depending on remedial works identified as part of the recommended structural survey. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Areas of render appear aged. Evidence of cracking, bossed render and spalling. | Carry out repairs where necessary to external render prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed; Single glazed windows are aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steel framed; Single glazed windows are aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Leaf External Timber doors appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Leaf External Timber door appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Repaint rendered areas following repair works; Remove excessive vegetation (Ivy) growing up the walls and clean brickwork. | Carry out external decoration works. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Flat roof covering appears aged and passed intended design life. There is evidence of various leaks throughout the building. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rainwater goods appear to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to Site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External luminaires appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (MEM) Isolator appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (Memshield 2) Distribution Boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring Systems - Small Power appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring Systems - Lighting appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal light fittings appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of some newer LED emergency light fittings; However, the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System throughout the site appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone/Data Systems appear aged throughout and passed intended design life. (Inc. 1No. aged data/comms rack in the basement plant room) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Basement Plant Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls. | Carry out a schedule of repairs to walls prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Plastered ceilings in some rooms have been damaged due to water ingress. | Repair and replaster ceilings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Suspended Ceiling areas appear aged and passed intended design life. Evidence of broken, stained and missing tiles. Ceiling grid also appears aged and showing signs of wear & tear. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | All floor coverings appeared aged and passed intended design life. Wear & tear evident throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed furniture in staff kitchen area and throughout the floor level appeared aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some evidence of recent decoration works; However, there are still some areas that require redecoration as wear & tear was noted at time of survey. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating system pipework appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat Emitters (Radiators) appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Hot & Cold Water Systems | Distribution | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 3No. Point of use instant hot water boilers appear aged and approaching the end of their intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary Ware all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No. Local extract fan appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  | New Medical Gas Alarm Panel appeared in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No. (Memshield 2) distribution boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Distribution Boards | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No. Hagar consumer unit (plastic enclosure) appears aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | There is evidence of newer LED light fittings; However, some old fluorescent light fittings remain in situ that appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone/Data Systems appear aged throughout and passed intended design life. (Inc. 2No. Aged data/comms racks) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Estates + Ducts + Plant Rooms | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some cracking noted to external render. | Repair external render. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aluminium framed double glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external timber double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external aluminium and glazed single door appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external aluminium and glazed double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No aluminium and glazed double sliding door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Automatic Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 3No aluminium and glazed double sliding door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external render appears to be aged and worn. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Aluminium profile sheet pitched roof covering appears to be in reasonably good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No flat roof light appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | Aluminium rain water goods appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Pressurisation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No LPHW pressurisation unit within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No heating dosing pot within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No Horizontal calorifiers within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No plate heat exchangers within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No plate heat exchangers within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 6 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No heating pumps within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Water softening plant within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Cold water storage tanks within level 5 plant room appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No hot water pump within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No LPHW pumps within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No supply & extract AHUs within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No supply & extract AHUs within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No inline extract fan to level 5 flat roof area appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No inline extract fans to level 5 flat roof area appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No fume extract fans within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  | Ventilation distribution appears to be in reasonably good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No York chillers to level 5 flat roof area appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No chilled water dosing pot within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of chilled water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Rycroft chilled water buffer vessel within level 5 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Chilled Water Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No chilled water pumps within level 5 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No 2500KG 33 person passenger lifts appear to be aged and at end of recommended design life, circa 1997. (Lifts 6 & 7). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No 1500KG 20 person passenger lift appears to be aged and at end of recommended design life, circa 1997. (Lift 8). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within lift replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within external LV switch room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Wet And Dry Risers | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | All | All | Miscellaneous | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Chloride Bardic battery charging unit within level 3 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No Staff Kitchens, & Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No surgeons panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No local intercom system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No Staff Kitchens & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No electrical tube heater within Lift No8 motor room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No medical vacuum pump set within plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No dryer unit within plant room appears to be aged and at end of recommended design life, circa 1997. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 5 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Doors | B | 6 |  |  | 0 |  | 1No single door appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Doors | B | 6 |  |  | 0 |  | Some double door sets appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Jubilee Wing | Level 6 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor defects noted to some areas of external wall. | Carry out necessary repairs. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber doors are rotting, delaminating and generally in a poor, aged condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber cladding to room at roof level adjacent to AHU appears aged and in poor condition with some parts missing. | Repair timber cladding. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | External decoration to timber cladding in some areas; Steel staircases and steel handrails along the access walkways to Supplies department is aged and in poor condition. | Carry out schedule of external redecoration works. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Roof appears aged and passed intended design life. Evidence of previous repairs and also slipped, damaged and missing slates to main pitched roof areas. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Roof | Coverings - Flat | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Some areas of wear & tear evident; especially where there is metal grid flooring sat straight on the flat roof covering. Also areas where water gathers were noted on the fire escape route. | Budget cost for lifecycle wear & tear replacement that is anticipated to some areas of flat roof | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Georgian wired rooflights appear aged and passed intended design life. Lifecycle replacement required. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of rainwater goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | External Building Works | Fire Escapes | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steel fire escape / plant access staircase (from Level 4 to AHU/Chiller plant area) is in a poor decorative state and as a result there is moderate / heavy corrosion evident. | It may be possible to cut-out and replace affected areas of steelwork but budget cost here allows for replacement of the staircase. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 2 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Roof mounted AHU appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Roof mounted supply and extract packaged AHU appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged Vent-Axia ducted extract fan to flat roof area appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Small ducted extract fan adjacent to main electrical incoming room (externally accessed) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Chiller to roof level supplying chilled water to cooling for AHU and MRI areas is aged and passed intended design life. Covers were noted to be hanging off. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Chilled water distribution appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Chilled Water Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. Chilled water pumps are nearing end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 2No Abbey Lift Care 2100KG 28 person passenger lifts appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Lifts & Hoists | Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Earlswood goods lift appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 2 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | All | All | Miscellaneous | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | The majority of floor coverings appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Staff Kitchen). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No Staff Kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No Reception Desk). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Staff Kitchen). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 9No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Plastered and suspended ceilings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed furniture appears to be aged and at end of recommended design life. (1No Staff Kitchen). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Main Building | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Windows | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Minor defects and age related wear & tear noted to window frames and seals. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Doors | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | External Double Steel Door - Access to roof from Level 5 Lift/Stairs lobby 003 appear aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Automatic Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No. Aluminium Automatic Sliding Doors appear aged. Signs of wear & tear evident; doors are approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Corrosion noted to bottom of column at the main entrance to building. | Prepare and repaint column | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Detritus noted to fronts of the rounded profile of the aluminium roof edges. | Budget cost to clean & repaint if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Roof | Coverings - Flat | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Roof covering appears aged with evidence of previous repairs. The covering was also very slippy with no safe access to the external Mitsubishi VRF unit situated on the flat roof. | Budget cost to clean flat roof; survey condition & integrity of the roof covering and carry out repairs if required. Also install walkway matting for access to plant. *NOTE - Additional budget may be required if decided that the roof covering (256m²) needs to be replaced. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Ventilation Plant | B | 7 |  |  | 0 |  | 1No. Supply AHU (Lennox Type NA40/2001 - Circa 2001 in Level 5 Plant Rm); appears in good order but lifecycle replacement anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Extract Plant | B | 10 |  |  | 0 |  | 1No. Extract AHU (Ref: New Extension E - Circa 2001 in Level 5 Plant Rm); appears in good order but lifecycle replacement anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Extract Plant | B | 10 |  |  | 0 |  | 1No. Dirty Extract AHU (Ref: Fracture Clinic in Level 5 Plant Rm); appears in good order but lifecycle replacement anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Distribution | B | 10 |  |  | 0 |  | Ventilation ductwork & lagging appears in good order but lifecycle replacement anticipated at the same time as the AHU's. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. External VRF unit appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Controls | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | 1No. Control Panel (MCC4) appears in good order but lifecycle replacement anticipated. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Ventilation Systems | Insulation | B | 10 |  |  | 0 |  | Cost to replace insulation is included within the ventilation systems distribution replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Lifts & Hoists | Passenger | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Passenger lift appears aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  | Lift control panel on Level 5 appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | External luminaires appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Communication Systems | Building Management systems | B | 8 |  |  | 0 |  | 1No. BMS Outstation - TREND NDP HMI Screen appears in good order; However, lifecycle replacement anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls; Age related wear & tear evident. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Plastered areas appear aged; Cracks & water staining noted at time of survey. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceiling appears aged with areas of staining and damage noted at time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings appear aged and passed intended design life. Wear & tear noted throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber doors appear aged and passed intended design life. Wear & tear to doors evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and passed intended design life. Wear & tear to doors evident. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed furniture in staff room kitchen area; office area and the main reception desk all appears aged and passed intended design life. Lifecycle wear & tear evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor appears aged; signs of wear & tear evident throughout. | Redecoration required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Long term lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating pipework appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating radiators appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace included as part of the heating system pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot & Cold distribution pipework; Although there is some evidence of newer pipework where local refurbishment / alteration of services has taken place; generally the pipework appears aged and passed intended design life | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace included as part of the hot & cold water system pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. LV Switch Panel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (small) Distribution Boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (large) Distribution Boards appear aged and passed intended design life. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Evidence of newer LED fittings; However, these now appear aged. Lifecycle replacement anticipated. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of newer LED emergency light fittings; However, the wiring is presumed original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System throughout the site appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone / Data Systems appear aged and passed intended design life throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls; Age related wear & tear evident. | Carr out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Plastered areas appear aged; Cracks & water staining noted at time of survey. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceiling appears aged with areas of staining and damage noted at time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings appear aged and passed intended design life. Wear & tear noted throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber doors appear aged and passed intended design life. Wear & tear to doors evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and passed intended design life. Wear & tear to doors evident. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed furniture in staff room kitchen area appears aged and passed intended design life. Lifecycle wear & tear evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor appears aged; signs of wear & tear evident throughout. | Redecoration required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Long term lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating pipework appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating radiators appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace included as part of the heating system pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot & Cold distribution pipework; Although there is some evidence of newer pipework where local refurbishment / alteration of services has taken place; generally the pipework appears aged and passed intended design life | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace included as part of the hot & cold water system pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. LV Switch Panel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (small) Distribution Boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (large) Distribution Boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Evidence of newer LED fittings; However, these now appear aged. Lifecycle replacement anticipated. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of newer LED emergency light fittings; However, the wiring is presumed original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System throughout the site appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone / Data Systems appear aged and passed intended design life throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Evidence of damp and plaster coming off the wall around the steel door leading on to flat roof on Level 5 Lift/Stairs Lobby 003 area. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceiling tiles to Lift/Stairs Lobby area on Level 5 are either missing, damaged or dirty. | Replace ceiling in this area. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Painted concrete floors have evidence of lifecycle wear & tear. | Repaint floor throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Double timber doors in to Plant Room 004 appear in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor appears aged; signs of wear & tear evident throughout. | Redecoration required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Long term lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Heating Systems | Pipework | B |  |  |  | 0 |  | Heating pipework to AHU appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Heating Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (large) Distribution Boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Evidence of newer LED fittings; However, these now appear aged; Some fittings have been retro fitted with LED tubes and some old fluorescent fittings still remain in situ. Lifecycle replacement anticipated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of newer LED emergency light fittings; However, the wiring is presumed original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System throughout the site appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Marnham Wing | Level 5 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Severe spalling noted to low level brick work on the West façade. | Recommend a structural survey of the brickwork / walls. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Areas of spalling noted to brickwork and mortar on bottom corner of wall adjacent to fire escape. | Carry out necessary repairs to brickwork and re-point where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Windows are aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Steel framed doors (single glazed) all appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Doors | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | Double glazed UPVC door is aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Timber / UPVC Detail | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | Timber soffits & facias on roof top plant rooms appear aged and approaching end of intended design life. Wear & tear visible. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Timber / UPVC Detail | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | Timber external cladding to roof top plant room appears aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External decoration of concrete structure appears aged; wear & tear evident. | Redecorate. *NOTE - Cost includes access equipment that will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | External decoration of metal fire escape stair cases; fire escape enclosure and metal hand rails all appear aged with wear & tear noted. | Prep & paint external metal work. *NOTE - Cost includes access equipment for fire escape enclosure. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Roof coverings appear aged and passed intended design life. Evidence of leaks; Also cracking and ponding to some areas. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Roof | Roof Lights | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Skylight over ground floor appears in good order, however appears dirty. | Clean. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rainwater goods are internally fixed and presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | PVC rainwater goods also appear aged and passed intended design life; evidence of wear & tear and some joints coming apart. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | Fire escape appears in good order structurally; However, there was evidence of corrosion. | *NOTE - See comment above for redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Pressurisation Plant | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No. Heating pressurisation unit & expansion vessel appears aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Calorifier (Located L1 - Plant Rm. 001) appears aged and passed intended design life. Damage noted to insulation. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Calorifier (Located L5 - Plant Rm. 002) appears aged, (Circa 25/11/1988) and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. LPHW Control Panel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Steam blow-down vessel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (Horizontal - Twin) Steam > appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steam & condensate pipework appears aged and passed intended design life. Various leaks evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (Grundfos - Twin Head) Heating Circulation Pumps appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (Single - Belt Driven) LPHW CT Pumps appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating Systems | Heating Pumps | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 4No. (Grundfos - Single) Heating Circulation Pumps appear aged and approaching end of intended design life. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. CWST's (Approx 1.5m x 1.5m x 5m) Located in Level 5 Plant Rm. 002 appear aged and passed intended design life. Wear & tear evident and some tank lagging noted to be missing. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. CWST's (Approx 1m x 1m x 1.5m) Located in Level 5 Plant Rm. 002 appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | B |  |  |  | 0 |  | 1No. M.W.S Tank appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No water softening unit appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No AHU Located in Level 5 - Plant Rm.002 appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Ventilation Ductwork throughout appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Split AC System (External condenser on roof outside Level 5 - Plant Rm. 002 appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No. Horizontal dry air coolers appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Computer Rm. AC Control Panel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No MCCP (MCC2). AHU Fan Control Panel appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 1No. Passenger lift appears in good order |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  | 1No. Passenger lift control panel & Brake resistor appear in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Main Incoming Switch (Fused Switch) Located in Level 1 Plant Rm.001 appears aged and passed intended design life. (Inst. Date:09/08/1985) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No LV Panel (ICW Switchgear) Located in Level 1 Plant Rm.001 appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  | Lightning protection appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | External light fittings appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Electrical Systems | Luminaires External | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | External Emergency Light Fittings appear to be showing signs of wear & tear from the external elements. Lifecycle replacement anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Miscellaneous (Block) | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No. Submersible Pump located in Level 1 Plant Rm.001 appears to be cutting in & out on a regular basis due to water leak from mains water supply pipe. Wear & tear anticipated due to excessive operation. | Lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | All | All | Miscellaneous | Miscellaneous (Block) | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is a water leak from the mains water supply pipework that is entering the plant room from the service duct and running down the wall and into the sump in the corner of the plant room. | Budget cost to repair pipework and rectify the leak. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Areas of damage & defects noted to concrete walls. There is water constantly running down the wall from the mains water supply leak in the service duct also. | Carry out a schedule of repairs to walls prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Level 1 _ Plant Rm. 001 concrete floor was noted to be uneven in places and various areas within the plant room had water on the floor. | Budget cost to rectify issues. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor (white-wash) to plant room walls is aged with evidence of wear & tear. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All heating pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No. Local extract fans appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Level 1 - Plant Rm. Switchgear reported at block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | DB appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; all appeared aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; all appeared aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Evidence of newer LED Light Fittings; however, lifecycle wear & tear anticipated. | Long term lifecycle replacement anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of newer LED Emergency Light Fittings; however, the wiring is presumed to be original, aged and passed intended design life. Lifecycle wear & tear of the emergency light fittings due to ambient temperature of plant room also anticipated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System throughout the site appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls. | Carry out a schedule of repairs to walls prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Plastered Ceiling areas appear in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Suspended Ceiling areas appear aged and passed intended design life. Evidence of broken, stained and missing tiles. Ceiling grid also appears aged and showing signs of wear & tear. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Vaulted Glass Brick / Concrete Skylight appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | All floor coverings appeared aged and passed intended design life. Wear & tear evident throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Internal sliding gate. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed furniture in staff kitchen area and throughout the floor level appeared aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is aged with evidence of wear & tear. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating system pipework appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat Emitters (Radiators) appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary Ware all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fan appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. LV Panel (ICW Switchgear) appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (small - Bill) Distribution boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (medium) Distribution boards appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | There is evidence of some newer LED light fittings; However, some old fluorescent light fittings remain in situ that appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of some newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone/Data Systems appear aged throughout and passed intended design life. (Inc. 2No. Aged data/comms racks) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Areas of plastered ceiling appear aged with evidence of cracking. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Areas of suspended ceiling appear aged with evidence of dirty, damaged and missing tiles. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout appear to be aged and passed intended design life. Wear & tear is evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | All unit furniture throughout appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is aged with evidence of wear & tear. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating distribution pipework all appears original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators all appears original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary Ware all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fan appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Medical Gas | Distribution | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Level 3 is now office / Admin space. Aged mgi AVSU's for O2 & VAC still remain in situ in the OFF position. No med gas outlets noted throughout the floor at time of survey | Budget cost to remove Med Gas System if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (small - Bill) Distribution boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Internal Luminaires | B | 10 |  |  | 0 |  | There is evidence of newer LED light fittings; However, lifecycle replacement is anticipated within the report period. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of some newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Alarms & Detection Systems | Security Systems | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | SECOM SD1+ Intruder Alarm (Circa 30/10/2009) Appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone/Data Systems appear aged throughout and passed intended design life. (Inc. 1No aged data/comms rack in room 234). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Communication Systems | Nurse Call Systems | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Level 3 is now office / Admin space. Aged Nurse Call system still remains in situ. No longer in use. | Budget cost to remove system if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Defects noted to walls. | Carry out a schedule of repairs prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Areas of plastered ceiling appear aged with evidence of cracking. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Areas of suspended ceiling appear aged with evidence of dirty, damaged and missing tiles. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout appear to be aged and passed intended design life. Wear & tear is evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single Timber door appears aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double Timber doors appear aged and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | All unit furniture throughout appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is aged with evidence of wear & tear. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating distribution pipework all appears original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators all appears original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary Ware all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fan appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Medical Gas | Distribution | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Level 4 is now office / Admin space. Aged mgi AVSU's for O2 & VAC still remain in situ in the OFF position. No med gas outlets noted throughout the floor at time of survey | Budget cost to remove Med Gas System if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. (small - Bill) Distribution boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Internal Luminaires | B | 10 |  |  | 0 |  | There is evidence of newer LED light fittings; However, lifecycle replacement is anticipated within the report period. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of some newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Alarms & Detection Systems | Security Systems | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | SECOM SD1+ Intruder Alarm (Circa 30/10/2009) Appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Telephone/Data Systems appear aged throughout and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Communication Systems | Nurse Call Systems | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Level 4 is now office / Admin space. Aged Nurse Call system still remains in situ. No longer in use. | Budget cost to remove system if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Door to lift motor enclosure appears in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is aged with evidence of wear & tear. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle wear & tear anticipated. | Lifecycle redecoration anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating distribution pipework all appears original; aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of heating system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | All hot & cold pipework appears original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost to replace insulation is included above as part of hot & cold water system pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal Drainage all appears aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | 2No EATON Isolators appear in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. (small - Bill) Distribution boards appear aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - small power; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring system - lighting; Presumed to be aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Internal Luminaires | B | 10 |  |  | 0 |  | There is evidence of newer LED light fittings; However, lifecycle replacement is anticipated within the report period. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | There is evidence of some newer LED emergency light fittings; However, some aged fittings remain in situ and the wiring is presumed to be original, aged and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Major (4) | 20 | High | Fire Alarm System appears aged throughout the Hospital and passed intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | QE Wing | Level 5 | All | Miscellaneous | Miscellaneous (Room) | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | High concrete partition wall between the 2 areas within the plant room is a potential trip / fall hazard. | Budget cost to install safe, suitable access over wall. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Structure | Foundations | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Tudor Wing is currently boarded up and not in use. Building appears to be falling into disrepair and requires a complete refurbishment if it is to be brought back in to use. | Full refurbishment is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Structure | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Structure | Frames | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Structure | Floors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Structure | Roofs | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Windows | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Roof | Rain Water Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Luminaires External | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Tudor Wing | All | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No aluminium and glazed double door set with automatic openers appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No aluminium and glazed double sliding door sets appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Automatic Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No aluminium and glazed double sliding door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Automatic Doors | B | 8 |  |  | 0 |  | 1No aluminium and glazed double sliding door set appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal railings appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external timber framework within courtyards appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Protective finish to some external timber fencing and gates appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched roof covering appears to be in reasonably good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Roof | Coverings - Pitched | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some insulation to the underside of pitched roof within plant room areas has become detached. | Replace and refix where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Roof | Coverings - Flat | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some inverted flat roof areas appear to be in poor condition. Pooling of water noted to external chiller area. | Replace / repair where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Roof | Roof Lights | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No pitched roof light appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aluminium rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external timber fencing and gates appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No fuel oil storage tank appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  | Gas supply pipework appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Boiler Plant | B |  |  |  | 0 |  | 9No Hamworthy Purewell Variheat gas fired condensing boilers appear to be in good condition, circa 2021. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Pressurisation Plant | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No chilled water pressurisation unit within second floor plant room (079) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Pressurisation Plant | B | 6 |  |  | 0 |  | 1No Hamworthy pressurisation unit within second floor plant room (079) appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Pressurisation Plant | B | 6 |  |  | 0 |  | 1No Hamworthy pressurisation unit within third floor plant room (001) appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | B |  |  |  | 0 |  | Heating dosing pots appear to be in good condition |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No Rycroft Ltd Horizontal calorifiers within second floor plant room (079) & third floor plant room (001) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Flues - Separate | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within second floor plant room (074) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No mechanical control panel within third floor plant room (001) appears to be redundant. | Budget cost for replacement if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within third floor chiller compound plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | See Site Physical Condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No VT heating pumps within third floor plant room (001) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No VT heating pumps within second floor plant room (079) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No CT heating pumps within second floor plant room (079) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No CT heating pumps within third floor plant room (001) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No boiler primary pumps within second floor plant room (079) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating Systems | Heating Pumps | B | 10 |  |  | 0 |  | 2No boiler primary pumps within third floor plant room (001) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B | 7 |  |  | 0 |  | Water treatment plant set within third floor plant room (006) appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Cold water storage tanks within second & third floor plant rooms appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No hot water pump within third floor plant room (001) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Pumps | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No hot water pump within third floor plant room (001) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Pumps | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 4No destratification pumps for hot water calorifiers within second floor plant room (079) & third floor plant room (001) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No simplex cold water booster sets within third floor plant room (006) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No raw water booster set within third floor plant room (006) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No inline supply fan within ground floor lift motor room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within second floor plant room (074) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within third floor plant room (001) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply & extract AHU within second floor plant room (074) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply & extract AHU within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No supply & extract AHU within second floor plant room (079) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No supply & extract AHUs within third floor plant room (006) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply & extract AHU within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No box extract fan (Paediatrics Isolation) within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No twin belt driven extract fans (Haematology & Biochemistry & Dirty Extract) within second floor plant room (074) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Smoke Extract) within second floor plant room (074) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Smoke Extract) within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Dirty Extract) within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Dirty Extract) within third floor plant room (001) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Smoke Extract) within third floor plant room (001) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No twin belt driven extract fan (Endoscopy Treatment & Recovery, Pathology & Dirty Extract) within third floor plant room (006) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Smoke Extract) within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No twin belt driven extract fan (Mortuary Extract) within third floor chiller compound plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No fume cupboard extract fans within second floor plant room (074) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No fume extract fans within third floor plant room (006) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  | Ventilation distribution appears to be in reasonably good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Daikin VRV systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 8 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 10 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No small refrigeration chillers within third floor chiller compound appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No small refrigeration chiller appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Air Blue chiller within second floor plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No York V-Type chillers within third floor chiller compound appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No chilled water dosing pot within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of chilled water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No chilled water buffer vessel within third floor plant room (006) appears to be aged and at end of recommended design life, circa 1990. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Chilled Water Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No chilled water pumps within third floor plant room (006) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 2No Liftec 2100KG 28 person passenger lifts appear to be in good condition, fully refurbished in 2008. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Lifts & Hoists | Goods | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No goods lift appears to be redundant. | Budget cost allowance for replacement if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within external LV switch room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within external LV switch room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within the ground floor appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No Durham Switchgear LV panels within the first floor appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within the first floor appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within the second floor appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Durham Switchgear LV panel within the second floor appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  | Lightening protection appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External lighting bollards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Mortuary Refrigerators | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of mortuary refrigerators and freezers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Air Tube Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Air tube system distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Air Tube Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 7No air tube terminal units appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Air Tube Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No air tube pump within second floor plant room (074) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Wet And Dry Risers | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | All | All | Miscellaneous | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Chloride Bardic battery charging unit within third floor plant room (006) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Staff Kitchen, 1No Reception Desk & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No Staff Kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No electrical panel heaters within lift motor room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 6 |  |  | 0 |  | The majority of sanitary ware appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No macerator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No Reception Desks, 4No Staff Kitchens & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No fume cupboards within labs appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Medical Gas | Manifolds | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No medical gas manifolds appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | First | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Doors | B | 6 |  |  | 0 |  | Some single doors appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Doors | B | 6 |  |  | 0 |  | Some double door sets appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Nurse Stations, 3No Staff Kitchens, 2No Reception Desks & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No Reception Desks). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 6 |  |  | 0 |  | Some sanitary ware appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No medical vacuum pump set within plant room (079) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Bedpan Disposal | B | 6 |  |  | 0 |  | 1No macerator appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Disinfection Equipment | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 2No Getinge washer/disinfector units appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Disinfection Equipment | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Getinge dryer unit appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | 2No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Second | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted floor finish within plant room appears to be aged and worn. | Repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No wash basin appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No duplex AGSS pump sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No medical vacuum pump set appears to be aged and at end of recommended design life, circa 1990. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No Heatrae Sadia P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Veralum Wing | Third Floor Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Structure | Foundations | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Windsor Day Hospital is currently boarded up and not in use. Building appears to be falling into disrepair and requires a complete refurbishment if it is to be brought back in to use. | Full refurbishment is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Structure | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Structure | Frames | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Structure | Floors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Structure | Roofs | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Windows | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Roof | Rain Water Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Luminaires External | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Day Hospital | All | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Structure | Foundations | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Windsor Wing is currently boarded up and not in use. Building appears to be falling into disrepair and requires a complete refurbishment if it is to be brought back in to use. | Full refurbishment is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Structure | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Structure | Frames | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Structure | Floors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Structure | Roofs | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Windows | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Roof | Rain Water Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Luminaires External | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Hemel Hempstead Hospital | Windsor Wing | All | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Refer to comments above under main element "Structure" & Sub element "Foundation". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | External Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Large parts of the site drainage system are aged and original and reportedly problematic. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Roads / Parking Areas | B | 6 |  |  | 0 |  | Tarmac road surfaces appear to be in reasonable condition | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Paths | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some wear and tear evident to tarmac paths. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Car Parks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wear and tear evident to tarmac car parks. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Fencing / Gates | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some aged and damaged perimeter fencing noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Barrier Entry & Exit Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Signage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Street Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | External Works | Ancillary Buildings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Fuel Supply / Storage / Distribution | B | 8 |  |  | 0 |  | Site gas main is in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Steam & Condensate Systems | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged steam and condensate main remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Hot & Cold Water Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some mains cold water services within the site are aged and original. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Heating Systems | N/A |  |  |  | 0 |  | Refer to comments above under "steam & condensate". |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Chilled Water / Refrigeration Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Medical and Industrial Gases | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Air Tube Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Mechanical Systems | Service Subways / Ducts | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | 1No HV transformer is aged and due replacement. 500Kva. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | 1No HV transformer is aged and due replacement. 300Kva. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | Cx | 0 | Certain (5) | Major (4) | 20 | High | 2No RMU's are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Major (4) | 20 | High | Aged HV cabling remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No 930kva generator circa 1996 is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No 1530kva generator circa 1996 is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Electrical | Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Communications | Telephone & Data Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Communications | Building Management systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Alarm Systems | Fire Alarm Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Security | CCTV Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Medical Gas Pipeline Services | Vacuum Insulated Evaporator | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Site | Site | Site | Miscellaneous | External Plant and Equipment | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage and missing mortar noted to some external brickwork. | Repair and repoint external brickwork where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Walls & Finishes | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to external metal cladding. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aluminium framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external timber single door appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | 1No external timber single door appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | 1No external timber double door set appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external concertina door appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external louvred vents appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof covering to main boiler room, gas meter room and generator room appears to be aged and at end if recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Roof | Rain Water Goods | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Some rainwater goods appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  | Gas supply pipework and gas boosters for boilers appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No B&B gas fired steam boilers appear to be aged and at end of recommended design life, circa 1979. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Boiler Treatment Plant | B | 6 |  |  | 0 |  | Dosing plant appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Flues - Separate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No flues for steam boilers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Flues - Separate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No flue gas analysers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No GFC Autoflame boiler control panels appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (Sewerage Pumps) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No Hotwells appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No external Blowdown Vessel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Heating Systems | Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No feed and expansion tank at high level appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Heating Systems | Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No treated water tanks at high level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No boiler feed pumps appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B | 6 |  |  | 0 |  | 1No packaged water softening plant appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No changeover panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Tiled flooring within main boiler house appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed work benches appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within Energy Centre Systems Steam & Condensate. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within Energy Centre Systems Steam & Condensate. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Medical Gas | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above within level 2. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Boiler House | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Structure | Walls | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some cracking noted to front elevation within brickwork. | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some mortar missing from external brickwork at low level. | Repoint external brickwork where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | UPVC double glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steel framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows to external corridor appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber detail to roof top plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external concrete structure appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external meatal roof edge protection appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | External fencing and gates to front elevation appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | Note; temporary external fire escape in place at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B |  |  |  | 0 |  | 1No Heatrae Sadia hot water cylinder within roof plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Ventilation Plant | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Ventilation system for kitchen and survey appears to be redundant. | Budget cost allowance if replacement is required in the future. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No roof extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Distribution | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within ventilation system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Room Split Chillers / Compressors | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No external condenser at roof level appears to be redundant. | Budget cost allowance if replacement is required in the future. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Chillers / Cooling Systems | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 3No external refrigeration chiller appears to be redundant. | Budget cost allowance if replacement is required in the future. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Chillers / Cooling Systems | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No external refrigeration chiller appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Controls | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within ventilation system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Ventilation Systems | Insulation | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within ventilation system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 0 electrical switch room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No Staff Kitchens). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No walk in fridge appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | Dx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No walk in fridges and 1No walk in freezer appears to be redundant. | Budget cost allowance if replacement is required in the future. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Intruder alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Staff kitchen). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No Staff Kitchen). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B | 8 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 11No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Catering Block (Old Spice of Life) | Roof Plant Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor damage noted to some external brickwork to front left elevation corner. | Repair/ replace damaged brickwork. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steel and timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber single doors to medical gas store appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | External timber cladding appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | External timber soffits and facias to external medical gas store appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to 4No sets of external metal gates and canopy frames appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external rain water goods appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to louvred vents to external medical gas store appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Fabric | Decoration | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Painted finish to external brick work appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Metal profile sheet roof to main building appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Pitched roof covering to estates external store and external medical gas store appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Rain water goods to external medical gas store appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Fencing / Gates | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Ryco horizontal calorifier appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steam pipework within plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Heating Systems | Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No feed and expansion tank located at high level within workshop appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Heating Systems | Heating Pumps | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No heating pump appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Dorman Smith LV panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Submains appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires to main building and medical gas store appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | BMS controls appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | All | All | Miscellaneous | Miscellaneous (Block) | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No small air compressor within workshop appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall finishes. | Repair wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted floor finish appears to be aged and worn throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of fixed furniture appears to be aged and at end of recommended design life. (1No Staff Kitchen, Work Benches & Fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Medical Gas | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Medical Gas | Alarm Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No medical gas alarm appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No Santon P.O.U water heaters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 3No Zip Aquapoint 3 P.O.U water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 6No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Intruder alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Estates | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor cracking noted to some external brickwork. | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 6No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 6No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No aluminium and glazed double sliding door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Automatic Doors | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No aluminium and glazed double sliding door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Automatic Doors | B | 6 |  |  | 0 |  | 2No aluminium and glazed double door sets with automatic openers appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Timber / UPVC Detail | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some damaged / missing soffits noted. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal canopies appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some profile sheet pitched roof appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some flat roof coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Roof | Roof Lights | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some roof lights appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | Rain water goods appear to be in reasonably good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No heating dosing pots within level -1 plant room appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Alfa Laval plate heat exchanger within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No horizontal calorifiers within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 0 appears to be aged and at end of recommended design life. (Day Surgery Heating). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No fire damper control panel within level 0 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level -1 plant room appears to be aged and at end of recommended design life. (Pumps). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No heating pumps within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Water softening plant within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Aquaboss R/O Unit within level 2 roof plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No small steel cold water storage tanks within level 2 roof plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Hot & Cold Water Systems | Pumps | B | 10 |  |  | 0 |  | 2No hot water pumps within level -1 plant room appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No Moducel supply & extract AHUs within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No Moducel supply & extract AHUs within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Extract Plant | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of ventilation distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 8 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | B |  |  |  | 0 |  | 2No external Daikin V Type chillers appears to be in good condition, circa 2021. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No chilled water dosing pot within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of chilled water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No chilled water buffer vessel within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chilled Water Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No chilled water pumps within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Chilled Water Pumps | B | 8 |  |  | 0 |  | 2No chilled water pumps within level -1 plant room appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Controls | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel within level -1 plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 0 appears to be aged and at end of recommended design life. (Atrium Ventilation Control Panel) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Ventilation Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above within ventilation distribution. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Hydraulic Lift Pack for passenger lift appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | No access, maintained by RJP Power Networks. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No LV panels within level 0 appear to be aged and at end of recommended design life. (Room 1.210A). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No LV panels within level 0 appear to be aged and at end of recommended design life. (Room 1.372). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Switchgear | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No large incoming LV panel within level -1 plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of the Trend BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Miscellaneous | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No central battery units within level 2 roof plant room appear to be aged and at end of recommended design life | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | All | All | Miscellaneous | Miscellaneous | B | 10 |  |  | 0 |  | 8No Starkstrom IPS / UPS units within level -1 plant room appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No Nurse Station). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Manifolds | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No medical gas manifolds appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 3No Atlas Copco air compressors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 2No compressed air receiver vessels appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 1No medical vacuum pump set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No macerator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 10No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No internal local intercom system for Day Surgery appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Scantronic Intruder alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some metal suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fibre suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | Some floor coverings appear to be good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (3No Staff Kitchens & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (4No Staff Kitchens & Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (3No Reception Desks). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No Staff Kitchen). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 6 |  |  | 0 |  | Some sanitary ware appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 5No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 6 |  |  | 0 |  | 1No Zip P.O.U local water heaters appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 10 |  |  | 0 |  | 1No Zip P.O.U local water heaters appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Switchgear | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 1No isolator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Intruder alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No intercom system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Alarms & Detection Systems | Security Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 2No intercom systems appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some panic alarm systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Communication Systems | Nurse Call Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some nurse call systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Internal Luminaires | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Internal luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Electrical Systems | Emergency Luminaires | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Gloucester Wing | Level 2 Plant Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Structure | Frames | B |  |  |  | 0 |  | Instances of potential carbonation of concrete were reported in 2018. At the time evidence of core sampling was noted and budget costs for remedial works were provided by Nifes. Upon visual inspection in 2023 no evidence of spalling concrete and exposed rebar can be identified. | Currently appears to be in good condition. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some minor damage noted to external brickwork. | Repair / replace external brickwork where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No external timber double door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external roller shutter door appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber and steel railings to balcony areas and escape staircase to the rear appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Pitched roof covering appears to be aged and at end of recommended design life, water ingress noted to some areas at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of flat roof coverings to appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single glazed roof light to centre of the building appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods are assumed to be original and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | External fire escapes appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No horizontal steam calorifiers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No horizontal steam calorifiers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level -1 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No mechanical control panels within level -1 plantroom appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate receiver vessel including pumps within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No heating pumps appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  | Water softening plant within main plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Cold water storage tanks within level 7 water tank room and basement plant room appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No hot water circulation pumps appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Hot & Cold Water Systems | Pumps | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Lowara hot water booster set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Hot & Cold Water Systems | Pumps | B |  |  |  | 0 |  | 1No cold water booster set appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Extract fan units appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Ventilation distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | 1No A.C split system appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No chiller on level 5 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 3 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No Liftec 2040KG 27 person passenger lifts appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within lift replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Dorman Smith LV panel within level 6 lift motor room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Dorman Smith LV panel within level 3 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Dorman Smith LV panel within level 2 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Dorman Smith LV panel within level 0 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No Dorman Smith LV panels within level -1 switch room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Barduct rising busbar system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Electrical Systems | Luminaires External | B | 6 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of the BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | All | All | Miscellaneous | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Medical Gas | Alarm Systems | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 2No medical gas alarms appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fire alarm system appears to be in good condition, however 1No fire alarm panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No Staff Kitchens & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some double door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (3No Staff kitchens & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some panic alarm systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | Some floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No Staff Kitchens, 1No Nurse Station & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No staff kitchens). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No Reception Desk). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Medical Gas | Outlets | B |  |  |  | 0 |  | Outlets appear to have been updated. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage and high level cracking noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | The majority of floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No staff kitchen, 1No Nurse Station & Fixed Units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Heating Systems | Heat Emitters | B |  |  |  | 0 |  | Heat emitters appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No macerator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | B | 6 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Wandsworth nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Doors | B | 6 |  |  | 0 |  | Some single doors appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 1No distribution board appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 6 Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Moynihan Wing | Level 7 Water Tank Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of timber framed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 7No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No aluminium and glazed double door sets with automatic openers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber soffits and facias appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external concrete structure appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched roof covering appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No plate heat exchangers within external plant room (003) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No steam to LTHW calorifiers within external plant room (003) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No 150L water heaters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within external plant room (003) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Condensate receiver vessel and associated pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Heating Systems | Header Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No feed and expansion tank to the first floor appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No heating circulation pumps appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No small steel cold water storage tank within level 3 roof space appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Hot & Cold Water Systems | Pumps | B | 10 |  |  | 0 |  | 1No hot water secondary pump within external plant room (003) appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No small supply AHU within level 3 roof space appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Nuaire box extract fans within level 3 roof space appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No box extract fan at roof level appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B |  |  |  | 0 |  | 6No Mitsubishi A.C split systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | B |  |  |  | 0 |  | 3No external A.C condensers for Balair AHU appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 0 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Nuaire mechanical control panel within level 2 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Controls | B | 10 |  |  | 0 |  | 1No external mechanical control panel at ground level appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No 2100KG 28 person passenger lifts appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within lift replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within external switch room (002) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 3 electrical switch room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Trend BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Hydrotherapy Pool | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Hydrotherapy pool and associated plant and equipment was noted to be out of use at the time of survey. | No cost allowance given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | All | All | Miscellaneous | Miscellaneous (Block) | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some plastered ceiling finishes appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required.(1No Staff Kitchen). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some internal decorations appear to be aged and approaching end of recommended design life. | Lifecycle redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 3No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  | 1No medical gas alarm appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 10 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Intruder alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Wiring Systems - Power | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Internal Luminaires | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  | Currently under refurbishment, no access at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Staff kitchen, 1No Nurse Station & Fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life.(Fixed Units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  | 1No medical gas alarm appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | 1No duplex AGSS pump set appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No macerator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | 1No intercom system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Wandsworth nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some painted floor finish appears to be aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No single door appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. (Lift Motor & Switch Room Only). | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Runcie Wing | Level 3 Roof Space | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | UPVC double glazed windows appear to be aged and at end of recommended design life, the majority of units appear to have blown seals and moisture ingress. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | UPVC and glazed single doors appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  | Timber soffits appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal porch support appears to be aged and worn. | Prepare and repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Metal profile sheet pitched roof covering appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Roof | Rain Water Goods | B | 8 |  |  | 0 |  | Rainwater goods appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  | Gas pipework appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Boiler Plant | B |  |  |  | 0 |  | 2No Hamworthy Purewell gas fired boilers appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Pressurisation Plant | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 1No heating pressurisation unit appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Boiler Treatment Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No heating dosing pot appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | DHW Storage / Non Storage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No horizontal hot water storage tank within roof tank room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Flues - Separate | B |  |  |  | 0 |  | Flues and dilution fan appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating Systems | Heating Pumps | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Grundfos duplex heating pump set (AHU circuit) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating Systems | Heating Pumps | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Grundfos duplex heating pump set (Radiator circuit) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating Systems | Heating Pumps | B | 8 |  |  | 0 |  | 1No Lowara duplex primary heating pump set appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating Systems | Heating Pumps | B | 8 |  |  | 0 |  | 2No Lowara boiler shunt pumps appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B | 8 |  |  | 0 |  | Cold water storage tank within roof tank room appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Hot & Cold Water Systems | Pumps | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Grundfos duplex hot water pump set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Ventilation Plant | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No supply AHU within roof tank room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Extract Plant | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within Energy Centre Systems Controls/Meters. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Note; switchgear reported at floor level within this report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Submains appear to be original and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Lightning Protection | B | 8 |  |  | 0 |  | Lightening protection appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Double door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of fixed furniture appears to be aged and at end of recommended design life. (2No Reception Desks, 1No Staff Kitchen & Fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some sanitary ware appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 3No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 6No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Intruder alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Nurse call system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted floor finish appears to be aged and worn. | Repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
St Albans City Hospital | Waverley Wing | Level 2 Roof Tank Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | External Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of underground drains are original 1960s and later and few problems arising (other than some inadequate bore sizes given increased demand on the system). Blockages are generally tackled via CCTV investigation and subsequent dynamic jetting or similar. | Given their age, some repairs / replacement likely. Replace estimated 300m. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Roads / Parking Areas | B | 7 |  |  | 0 |  | Lifecycle resurfacing to site roadways. | Resurface roadways. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Paths | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor wear and tear to occasional tarmac path. | Carry out suitable lifecycle repairs. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Car Parks | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Various smaller staff and public car parks around the site with differing conditions of tarmac surface. Multi-storey car park in a good condition. | Resurface small car parks. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Fencing / Gates | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some lifecycle replacements to timber panel fencing to perimeter. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Barrier Entry & Exit Systems | B | 8 |  |  | 0 |  | Various car park barriers to smaller car parks - lifecycle replacement. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Signage | B |  |  |  | 0 |  | General identification signage site-wide appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Street Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | External Works | Ancillary Buildings | N/A |  |  |  | 0 |  | Refer to individual building reports. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Fuel Supply / Storage / Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Site gas main is predominantly aged and original remaining in situ beyond intended design life. | Replace aged gas mains. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Steam & Condensate Systems | Cx | 0 | Certain (5) | Major (4) | 20 | High | Steam and condensate mains serving site wide plant room is aged and original. Ongoing problems reported at the time of survey. | Replace steam and condensate main. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Hot & Cold Water Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Majority of cold water services and site mains are aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Heating Systems | N/A |  |  |  | 0 |  | Heating systems within buildings have been reported within individual block reports. Site steam & condensate main has been reported above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Chilled Water / Refrigeration Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Medical and Industrial Gases | B |  |  |  | 0 |  | Responsibility of BOC. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Air Tube Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Mechanical Systems | Service Subways / Ducts | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Electrical | Sub Stations / Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Electrical | Electrical Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Site LV distribution cables are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Electrical | Lighting | B |  |  |  | 0 |  | Majority of external lighting to car park areas and roadways in a good condition with LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Communications | Telephone & Data Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Communications | Building Management systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Alarm Systems | Fire Alarm Systems | N/A |  |  |  | 0 |  | Reported at individual block level. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Security | CCTV Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Medical Gas Pipeline Services | Vacuum Insulated Evaporator | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Site | Site | Site | Miscellaneous | External Plant and Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Structure | Floors | C | 0 | Certain (5) | Major (4) | 20 | High | Issues reported with floor structures at the time of survey. Structural report has been requested from the Trust. Further conversations to be held with the Trust regarding the findings of the structural assessment and possible remedial work / cost to be included at a later date. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Windows | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Original windows are showing some wear and tear. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Doors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 3No Double steel door sets are in poor condition and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No double timber door set to chilled water plant room is noted to be in poor condition and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Automatic Doors | B | 8 |  |  | 0 |  | 1No Automatic sliding door sets appear to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor to external rendered finish is in poor condition with heavy staining noted. | External redecoration is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Fabric | Decoration | B | 7 |  |  | 0 |  | Minimal defects noted. | Also required in the long term in line with lifecycle. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Roof | Coverings - Flat | B |  |  |  | 0 |  | Profile sheet roof covering appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Pressurisation Plant | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No pressurisation unit for LTHW in roof level plant room is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Pressurisation Plant | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No pressurisation unit for chilled water located in external compound is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No Horizontal steam calorifiers for LTHW are aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No HW storage calorifiers are nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Controls / Meters | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No medium size control panel is aged and nearing end of design life to roof level plant room. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Controls / Meters | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No small size control panel is aged and nearing end of design life to roof level plant room. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  | Generator has recently been removed including day tank. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Energy Centre Systems | Steam and Condensate | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Steam and condensate pipework appears to be aged and is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Heating Systems | Heating Pumps | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No VT and 2No CT pumps and 2No shunt pumps are aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1no water softening system is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Sectional GRP water tanks appear to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Hot & Cold Water Systems | Pumps | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No triplex cold water booster pump set is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Ventilation Plant | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 6No AHU's to the roof level pant room are aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Extract Plant | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No dirty extract fan to roof level plant room is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Extract Plant | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 3No fume extracts located externally at roof level appear to be aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No AC split systems are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Chillers / Cooling Systems | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 2No external chillers are showing signs of wear and tear. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Chilled Water Distribution | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Chilled water pipework is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Chilled Water Pumps | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 1No chilled water pump located in external compound appears to be aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Controls | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 1No chilled water control panel is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Lifts & Hoists | Passenger | B | 8 |  |  | 0 |  | 3No passenger lifts appear to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Electrical Systems | Switchgear | B | 10 |  |  | 0 |  | 1No LV switchboard to ground floor electrical intake room is in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Electrical Systems | Sub-mains | B | 10 |  |  | 0 |  | Submains are generally in good condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some external light fittings are aged due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Communication Systems | Building Management systems | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | BMS system appears to be original and is nearing end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Air Tube Systems | B | 10 |  |  | 0 |  | Minimal defects noted to terminal units. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Wet And Dry Risers | B |  |  |  | 0 |  | Dry Riser appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor wall damage evident throughout floor level. | Undertake a scheme of internal wall repairs prior to internal redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Majority of floor coverings are worn, aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal single doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal double doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Staff and ward kitchens appear to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term in line with lifecycle. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Heating Systems | Pipework | B | 8 |  |  | 0 |  | Minimal defects noted to heating system pipework. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Heating Systems | Heat Emitters | B | 8 |  |  | 0 |  | Minimal defects noted to ceiling mounted radiant panels. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Heating Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Hot & Cold Water Systems | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Hot & Cold Water Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Manifolds | B | 8 |  |  | 0 |  | 1No medical Air manifold appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Outlets | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Alarm Systems | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Medical vacuum plant is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Medical air plant is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Distribution Boards | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Wiring Systems - Power | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Internal Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Minor wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Communication Systems | Telephone/Data Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Telecommunications appears to be original and is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Communication Systems | Nurse Call Systems | B | 8 |  |  | 0 |  | Codemlon Nurse call system appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor wall damage evident throughout floor level. | Undertake a scheme of internal wall repairs prior to internal redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Majority of floor coverings are worn, aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal single doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal double doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Staff kitchen appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term in line with lifecycle. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Heating Systems | Pipework | B | 8 |  |  | 0 |  | Minimal defects noted to heating system pipework. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Heating Systems | Heat Emitters | B | 8 |  |  | 0 |  | Minimal defects noted to ceiling mounted radiant panels. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Heating Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Hot & Cold Water Systems | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Hot & Cold Water Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Medical Gas | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Medical Gas | Outlets | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Medical Gas | Alarm Systems | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Distribution Boards | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Wiring Systems - Power | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Internal Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Minor wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Communication Systems | Telephone/Data Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Telecommunications appears to be original and is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Communication Systems | Nurse Call Systems | B | 8 |  |  | 0 |  | Codemlon Nurse call system appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor wall damage evident throughout floor level. | Undertake a scheme of internal wall repairs prior to internal redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Majority of floor coverings are worn, aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal single doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Doors | B | 8 |  |  | 0 |  | Minor wear and tear evident to internal double doors. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Staff and ward kitchens appear to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term in line with lifecycle. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Heating Systems | Pipework | B | 8 |  |  | 0 |  | Minimal defects noted to heating system pipework. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Heating Systems | Heat Emitters | B | 8 |  |  | 0 |  | Minimal defects noted to ceiling mounted radiant panels. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Heating Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Hot & Cold Water Systems | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Hot & Cold Water Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Medical Gas | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Medical Gas | Outlets | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Medical Gas | Alarm Systems | B | 8 |  |  | 0 |  | Cost included above as part of system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Distribution Boards | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Wiring Systems - Power | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Internal Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Minor wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Communication Systems | Telephone/Data Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Telecommunications appears to be original and is nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Communication Systems | Nurse Call Systems | B | 8 |  |  | 0 |  | Codemlon Nurse call system appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Vinyl flooring is noted to be in poor condition and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term in line with lifecycle. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Heating Systems | Pipework | B | 8 |  |  | 0 |  | Minimal defects noted to heating system pipework. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Heating Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Hot & Cold Water Systems | Distribution | B | 8 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Hot & Cold Water Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Medical Gas | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 6 |  |  | 0 |  | 2No AGSS pumps appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Distribution Boards | B | 10 |  |  | 0 |  | Minimal defects noted to Merlin Gerin Distribution Boards. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Wiring Systems - Power | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Internal Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Minor wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Wear and tear evident. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system is aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | AAU | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Structure | Foundations | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Structure | Frames | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various areas of poor pointing to external brick walls. Some stone cills to windows are damaged and in need of repair/complete replacement. Small areas of external render are cracked and detached from wall and as these have presumably been installed at some point in order to prevent potential water ingress, their current state will exacerbate the issue allowing water to penetrate the solid wall construction but not breathe. | Budget cost allowance for repairs to external walls, repointing works where necessary, repair/replacement of window cills and repairs/removal of defective render. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Majority of windows to the building are timber framed, sash style and original. Some are rotten and in a very poor condition compromising the integrity of the window and support for the glazing panes. Steel and aluminium replacement units are predominantly single glazed and similarly beyond intended design life. Window opening mechanisms and ironmongery is generally poor throughout. Occasional uPVC replacement window (including to second floor link corridor) is in a good condition. | Replace all old and poor condition windows. Note that the cost does not allow for any potential uplift as a result of the listed status. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various external timber doors are rotten, ill-fitting and generally worn. | Replace doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various timber fascias and soffits, particularly to offshots to rear courtyards, are in a poor condition and require replacement. | Budget cost allowance for replacement of damaged soffits and fascias. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External redecoration required to timber fascias and soffits (not already costed for replacement elsewhere in this report) and rendered surfaces of external walls e.g. to north-east elevation. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Fabric | Decoration | B | 7 |  |  | 0 |  | Lifecycle external redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Roof | Coverings - Pitched | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Pitched slate covered roof areas appear to be in a reasonable condition but occasional slipped and damaged slate will require repair. | Budget cost allowance for ongoing repairs to slate roof coverings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some areas of felt covering to flat roofs are aged and in a poor condition e.g. to rear of former Medical Records area and front entrance of Stores. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | uPVC rainwater goods are discoloured and leaks are evident at some joints. Cast rainwater goods are in a poor condition with leaks evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Tarmac surface to areas within courtyards is cracked and damaged. | Strip off and re-lay Tarmac wearing course. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | External Building Works | Fire Escapes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No. External steel fire escape staircases require redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No. Hamworthy Purewell gas fired boilers to boiler room are aged and due for lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Pressurisation Plant | B |  |  |  | 0 |  | Flamco pressurisation unit in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lifecycle replacement of Grundfos heating pumps to Boiler room. | Replace pumps: 2No. Single (£1250 each), twinset (£1450) and small single (£400). | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No. condenser units to entrance to Stores are aged and beyond intended design life. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | Large LV panel to Electrical Cupboard (externally accessed) appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  | External luminaires are generally in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Plaster damage and evidence of water ingress to walls within various areas of the building. Localised impact damage and damage from historic drainage leaks also requires rectification. Risk reflects presence of mould to some areas. | In the first instance, mould should be cleaned and removed throughout. Due to the age and solid wall construction type of the building, it may be necessary to dry-line and board the various affected areas. Budget cost allows for majority of the worst affected areas. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some plastered ceilings are in a poor condition due to historic water leaks and damp ingress. | Repair damaged plastered ceilings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Where installed fibre suspended ceilings are aged and worn. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Floor coverings showing signs of wear and tear throughout with damage noted to some areas causing trip hazards (costed within Statutory Compliance report). | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wood parquet flooring to areas e.g. former Medical Records requires sanding and re-finishing. | Prepare, sand and re-seal wooden flooring. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some aged and worn internal doors will require replacement as part of an internal programme of refurbishment. | Replace, note that Fire Doors are costed for replacement within Statutory Compliance report. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to fixed units to Kitchen areas, particularly within unoccupied areas. | Budget cost allowance to replace all aged and worn fixed units. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water distribution is aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aging fittings to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage systems are original and aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various local point-of-use domestic hot water heaters installed throughout will require lifecycle replacement. | Budget cost for replacement of various domestic hot water heaters, average cost per unit used. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various local distribution boards throughout the building, Crabtree, Dorman Smith and Bill all beyond design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of internal luminaires have been upgraded to LED fittings but some aging units still remain. | Replace aged light fittings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of emergency luminaires have been upgraded to LED fittings but some aging units still remain. | Replace aged emergency light fittings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some newer field devices but fire alarm panel and assumed wiring system is aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged and obsolete analogue systems to some areas. | Replace if required (some areas unoccupied at time of survey). | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Plaster damage and evidence of water ingress to walls within various areas of the building. Localised impact damage and damage from historic drainage leaks also requires rectification. | Due to the age and solid wall construction type of the building, it may be necessary to dry-line and board the various affected areas. Budget cost allows for majority of the worst affected areas. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some plastered ceilings are in a poor condition due to historic water leaks and damp ingress. | Repair damaged plastered ceilings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Floor coverings showing signs of wear and tear throughout with damage noted to some areas causing trip hazards (costed within Statutory Compliance report). | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some aged and worn internal doors will require replacement as part of an internal programme of refurbishment. | Replace, note that Fire Doors are costed for replacement within Statutory Compliance report. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to fixed units to Kitchen areas, particularly within unoccupied areas. | Budget cost allowance to replace all aged and worn fixed units. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water distribution is aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aging fittings to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage systems are original and aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various local point-of-use domestic hot water heaters installed throughout will require lifecycle replacement. | Budget cost for replacement of various domestic hot water heaters, average cost per unit used. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Various local distribution boards throughout the building, Crabtree, Dorman Smith and Bill all beyond design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of internal luminaires have been upgraded to LED fittings but some aging units still remain. | Replace aged light fittings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of emergency luminaires have been upgraded to LED fittings but some aging units still remain. | Replace aged emergency light fittings. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some newer field devices but fire alarm panel and assumed wiring system is aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged and obsolete analogue systems to some areas. | Replace if required (some areas unoccupied at time of survey). | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | First | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Floor coverings showing signs of wear and tear. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Fixed units to Meeting Room showing signs of wear and tear. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of wiring is aged and beyond intended design life. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some newer field devices but fire alarm panel and assumed wiring system is aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged and obsolete analogue systems to some areas. | Replace if required (some areas unoccupied at time of survey). | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Admin Block | Second | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Windows | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Doors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 1No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Doors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 1No external timber double door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Roof | Coverings - Flat | B | 8 |  |  | 0 |  | Flat roof coverings appear to be in reasonably good condition, however long term replacement of some areas will be required. | Some long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 7 |  |  | 0 |  | 1No A.C split system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 10 |  |  | 0 |  | 1No A.C split system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 2No 2500KG 33 person passenger lifts appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  | 2No hydraulic lift packs and control panels appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | 1No incoming LV panel within electrical intake/switch room (010086) appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | All | All | Miscellaneous | External CCTV | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall finishes. | Repair wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | The majority of floor coverings appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No staff kitchen & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No staff kitchens & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 6 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (Fixed units). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No staff kitchen, 1No reception desk & 1No nurse station.). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Heating Systems | Heat Emitters | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Some electrical panel heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Ventilation Systems | Local Extract | B | 6 |  |  | 0 |  | Local extract fans appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Ventilation Systems | Local Extract | B | 6 |  |  | 0 |  | 1No local extract fan appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Medical Gas | Distribution | B |  |  |  | 0 |  | Medical gas system appears to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Medical Gas | Manifolds | B |  |  |  | 0 |  | Medical gas manifold appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Medical Gas | Outlets | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | Medical vacuum pumps, air compressors and dryer unit appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | 4No macerators appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 3No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Power wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | The majority of internal luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | The majority of emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  | Telephone/data systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall finishes. | Repair wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | The majority of floor coverings appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No nurse station.). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Heating Systems | Heat Emitters | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Some electrical panel heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Ventilation Systems | Local Extract | B | 6 |  |  | 0 |  | Local extract fans appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Ventilation Systems | Local Extract | B | 6 |  |  | 0 |  | 1No local extract fan appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Medical Gas | Distribution | B |  |  |  | 0 |  | Medical gas system appears to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Medical Gas | Outlets | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | 1No macerator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Power wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | The majority of internal luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | The majority of emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  | Telephone/data systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Ambulatory Care Unit | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No timber framed single glazed window appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Windows | B | 6 |  |  | 0 |  | UPVC double glazed windows appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | 3No UPVC doors appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some timber facias and timber detail above windows appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external timber detail above windows appears to be aged and worn | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Fabric | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Painted finish to external metal gate appears to be aged and approaching end of recommended design life. | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched slate roof covering appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Roof | Roof Lights | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No light well cover to level -1 appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | Rain water goods appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No cast iron soil stack appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Walls | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Brick pillar to front elevation appears to be aged and damaged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Concrete fencing panels to front elevation appear to be aged and at end of recommended design life, exposed rebar noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Boiler Plant | B | 8 |  |  | 0 |  | Worcester gas fired boiler appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Heating Systems | Heating Pumps | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall finishes. | Repair wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Plastered ceilings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No double door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Walls appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Plastered and suspended ceilings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor covering within W.C appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | The majority of floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed furniture appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B |  |  |  | 0 |  | 1No Heatrae Sadia P.O.U local water heater appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Power wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Intercom systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some plastered ceilings appear to be aged and at end of recommended design life. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some single doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Fixed furniture to staff kitchen appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Power wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Beeches (62 Vicarage Road) | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Structure | Frames | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Flaking paintwork to external building support frame work. | Repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cladding is generally dirty and requires cleaning. | Clean cladding. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Windows | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Original double glazed powder coated aluminium frame windows in reasonable condition however approaching end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Doors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Original aluminium external doors in reasonable condition however approaching end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Automatic Doors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Automatic door sets to main entrance in serviceable condition however approaching end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Roof | Coverings - Flat | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | Flat roof coverings nearing end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Roof | Roof Lights | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Original roof lights nearing end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Boiler Plant | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 1 No. Potterton domestic gas fired boiler in serviceable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 2 No. 182 litre Andrews Water Heaters calorifiers in serviceable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. plant room control panel at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Heating Systems | Heating Pumps | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2 No. Grundfos heating pumps in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Hot & Cold Water Systems | Pumps | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1 No. Grundfos DHW pump in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 1 No. DAB 630 kg / 8 persons passenger lift in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External bulkhead light fittings are weathered and at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. Trend BMS outstation at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Floor coverings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed units in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | General wear and tear noted to décor throughout. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Heating Systems | Pipework | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Heating pipework and steel panel heat emitters in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Hot & Cold Water Systems | Distribution | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Hot & cold water distribution in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  | Sanitary ware in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 3 No. Eaton MEM distribution boards in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Wiring Systems - Power | B | 6 |  |  | 0 |  | Power wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B | 6 |  |  | 0 |  | Lighting wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceilings in reasonable condition however some areas of stained tiles noted. | Replace stained tiles. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Floor coverings in reasonable condition however nearing end of lifecycle. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed units in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | General wear and tear noted to décor throughout. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Heating Systems | Pipework | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Heating pipework and steel panel heat emitters in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Hot & Cold Water Systems | Distribution | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Hot & cold water distribution in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  | Sanitary ware in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Wiring Systems - Power | B | 6 |  |  | 0 |  | Power wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B | 6 |  |  | 0 |  | Lighting wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceilings in reasonable condition however some areas of stained tiles noted. | Replace stained tiles. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Floor coverings in reasonable condition however nearing end of lifecycle. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Internal doors in reasonable condition however 4 No. doors to consultants offices beginning to show signs of minor wear and tear. | Replace 4 No. single doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed units in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | General wear and tear noted to décor throughout. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Heating Systems | Pipework | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Heating pipework and steel panel heat emitters in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Hot & Cold Water Systems | Distribution | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Hot & cold water distribution in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  | Sanitary ware in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Wiring Systems - Power | B | 6 |  |  | 0 |  | Power wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B | 6 |  |  | 0 |  | Lighting wiring in reasonable condition. Lifecycle replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cardiac Centre | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Structure | Frames | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original PVCu frame double glaze windows at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External doors are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Timber / UPVC Detail | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Paintwork & treatment to timber cladding in reasonable condition. | Treat & repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Flat roof coverings at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original single glazed wired roof lights are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | PVCu rainwater goods appear worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 x LTHW shell & tube steam calorifier is heavily dated and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B |  |  |  | 0 |  | 2 No. Ryco vertical DHW steam fed calorifiers are in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Heating Systems | Heating Pumps | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1 No. Wilo heating circulation pump in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | GRP cold water storage tank above second floor corridor is original and at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2 No. DHW circulation pumps at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Room Split Chillers / Compressors | B |  |  |  | 0 |  | 1 No. 2021 Daiken split air condensing unit in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  | Manual goods lift redundant and not in use. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Fused switches at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Electrical Systems | Luminaires External | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | External light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | BMS system at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed kitchen units in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Eaton MEM distribution boards in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed kitchen units in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Eaton MEM distribution board in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Internal doors in reasonable condition however nearing end of lifecycle. | Replace 30 No. single & 18 No. double doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed kitchen units in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Eaton MEM distribution boards in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Alarms & Detection Systems | Security Systems | B | 6 |  |  | 0 |  | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cherry Tree House | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | Coping stones installed to the parapet wall to the front elevation. At the time of survey it was not possible to inspect these at closely but from ground level they appear to be reasonably well fixed. Consideration should be given to checking the condition of these in more detail to ensure that there is minimal risk of the stones becoming detached. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Occasional replacement uPVC double glazed window but majority are aged timber or metal framed single glazed units and generally in a poor condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Timber external doors are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  | Timber fascias and soffits appear to be in a reasonable condition although redecoration is required (costed elsewhere). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External redecoration required to timber fascias and soffits. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched slate covered roof areas appear sound. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Felt covering to flat roof is beyond design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rooflights to flat roof area are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | uPVC rainwater goods appear to be in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Boiler Plant | B |  |  |  | 0 |  | Ideal gas fired boiler in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Pressurisation Plant | B |  |  |  | 0 |  | Flamco pressurisation unit in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Calorifier to boiler room is aged and beyond design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating pumps at end of design life. | Replace 2No. Small (£400 each) and 1No. Larger (£680). | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Mitsubishi condenser unit is aged and beyond intended design life. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | Large LV panel to Electrical Cupboard (externally accessed) appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External luminaires are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings showing signs of wear and tear. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors appear adequate. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to fixed units to Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Radiators and pipework are aged. Some electric panel heaters to offices to rear. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Hot and cold water distribution is aged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aging fittings to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans to WCs and Kitchen areas. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged MEM isolators to Boiler Room. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Eaton Memshield distribution board to Electrical Cupboard (externally accessed) appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Condition of distribution boards and most fittings suggests wiring has been replaced. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Condition of distribution boards and most fittings suggests wiring has been replaced. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some newer field devices but Gent fire alarm panel and assumed wiring system is aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Clinical Engineering | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | External brick walls in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Windows | B | 8 |  |  | 0 |  | Timber framed, narrow-gauge double glazed windows are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber external door is delaminating at the base. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  | Timber fascias and soffits appear to be in a reasonable condition although redecoration is required (costed elsewhere). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External redecoration required to timber fascias and soffits. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched slate covered roof appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Roof | Rain Water Goods | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | uPVC rainwater goods are discolouring. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | External steel staircase to loft space appears to be in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | Services fed from adjacent Pathology building. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 10 |  |  | 0 |  | Various Daikin split units may require lifecycle replacement within the 10 year period. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cracks to ceiling finish within G07 and G13. | Further investigate to establish potential cause and subsequently complete any remedial works and repairs as necessary. Budget cost allowance. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Floor coverings showing signs of general wear and tear. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors appear adequate. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Internal Fabric & Fixtures | Decoration | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Heating Systems | Pipework | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | Heating pipework appears to be aged and due for lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Heating Systems | Heat Emitters | B |  |  |  | 0 |  | Radiators appear to be in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Ventilation Systems | Local Extract | B | 8 |  |  | 0 |  | Various local extract fans to WCs - lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Eaton Memshield 3 distribution board in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | Lifecycle replacement may be required within the 10 year period. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Cytology | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Original windows appear to be aged, in poor condition and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No external single timber door is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No external double timber doors are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Roof | Coverings - Flat | B | 8 |  |  | 0 |  | Minimal defects noted to flat roof covering at the time of survey. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Georgian wired roof light located on the roof is aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internally fixed rainwater goods appear to be original and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  | Oil storage tanks and associated filling lines appear to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Major (4) | 20 | High | 3No original steam boilers are aged circa 1980 and remain in situ beyond intended design life. Associated burners and controls will also require replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Pressurisation Plant | B |  |  |  | 0 |  | 1No Mikrofil Pressurisation Unit appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B |  |  |  | 0 |  | 1No PHE circa 2016 is in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No calorifier appears to be aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Flues - Separate | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Controls / Meters | B | 10 |  |  | 0 |  | 1No large control panel is in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Generators | B |  |  |  | 0 |  | 1No CHP circa 2016 appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate recovery unit is aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate pipework appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Energy Centre Systems | Steam and Condensate | B |  |  |  | 0 |  | 1No Hotwell and 1No softwell appear to be in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B | 6 |  |  | 0 |  | 1No chemical dosing station is in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B | 6 |  |  | 0 |  | 1No water softening station appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Cold water storage tank to second floor is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No feed expansion tank is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No mushroom extract fan located on the roof is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Extract Plant | B | 10 |  |  | 0 |  | 1No dust extract system appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 7 |  |  | 0 |  | Minor wear and tear evident to external condensers located on the roof. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Chillers / Cooling Systems | B | 10 |  |  | 0 |  | Minimal defects noted to 2No external chillers. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | Refer to site report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | 1No LV Switchboard appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Communication Systems | Building Management systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | All | All | Miscellaneous | Miscellaneous (Block) | B | 6 |  |  | 0 |  | 1No compressor appears to be in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Generally in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceiling appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Vinyl flooring appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No fitted kitchen appears to be aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Minor wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating system pipework appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some aged wiring evident within the main boiler house. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some aged wiring evident within the main boiler house. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some aged light fittings noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Generally in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceiling appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some aged vinyl flooring noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Doors | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some internal doors are aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Decoration | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Minor wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Internal Fabric & Fixtures | Decoration | B | 10 |  |  | 0 |  | Minimal defects noted. | Also required in the long term. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating system pipework appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Aged hot and cold water system is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Sanitary ware appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal drainage system appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some aged wiring evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some aged wiring evident. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Internal Luminaires | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | First | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings appear to be aged throughout.. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Doors | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some internal doors are aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged fitted kitchen units are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Minimal defects noted. | Also required in the long term. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating system pipework appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Aged hot and cold water system is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Sanitary ware appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal drainage system appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Internal Luminaires | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Minimal defects noted. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Estates & Boiler House | Second | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Structure | Frames | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Areas of decaying mortar joints across much of ground level external brickwork. | Rake out and repoint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single glaze timber sash windows are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber doors are worn and dated. Aluminium external doors to front elevation in reasonable condition. | Replace timber doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. automatic door set to front elevation main entrance in reasonable condition however nearing end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Timber fascia's and soffits are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Slate tile pitched roof coverings generally in reasonable condition however sporadic areas of slipped or weathered tiles are evident. | Replace defective tiles. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Roof | Coverings - Flat | B |  |  |  | 0 |  | Flat roof coverings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | PVCu rainwater goods appear worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3 No. Hamworthy Purewell gas fired boilers at end of design life | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1 No. c. 2004 300 litre Cetetherm calorifier at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. plant room control panel at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4 No. Grundfos heating pumps at end of lifecycle. Remaining 4 No. Grundfos heating pumps in good condition. | Replace 4 No. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  | 1 No. AquaTech Pressmain cold water booster set in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | 1 No. cold water storage tank to basement plant room in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2 No. Grundfos DHW pumps at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Ventilation Plant | B |  |  |  | 0 |  | 1 No. AHS externally mounted AHU in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Ventilation Plant | B | 6 |  |  | 0 |  | 1 No. externally mounted supply & extract AHU in serviceable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 2 No. Daiken & 2 No. Mitsubishi split air condensing units in reasonable condition. Lifecycle replacement. 1 No. 2020 Daiken unit in good condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. AHU control panel at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 1 No. Aritco passenger lift in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Electrical Systems | Luminaires External | B | 6 |  |  | 0 |  | External light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. Trend BMS outstation at end of lifecycle. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Wall, ceiling and floor finishes generally deemed adequate for use as plant room and stores. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Wall, ceiling and floor finishes generally deemed adequate for use as plant room and stores. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Wall, ceiling and floor finishes generally deemed adequate for use as plant room and stores. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  | No emergency lighting noted - refer to Statutory Compliance report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Detection provision is limited - refer to Statutory Compliance report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Suspended ceilings to Medical Records are worn and dated. Suspended ceilings to remaining areas in reasonable condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings to Medical Records are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | Floor coverings to Dermatology Centre and Blood Clinic in reasonable condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal doors to Medical Records areas at end of lifecycle. Internal doors to remaining areas in reasonable condition. | Replace 6 No. single & 3 No. double doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed units to Dermatology Centre and Blood Clinic in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor to Medical Records is worn and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration of Medical Records. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Internal Fabric & Fixtures | Decoration | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Décor to Dermatology Centre and Blood Clinic in reasonable condition. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and steel panel heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware to Medical Records is dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Dated wiring to Medical Records. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Dated wiring to Medical Records. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Dated light fittings to Medical Records. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency lighting in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Nurse call system to Dermatology Centre appears dated. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed units in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Worn and dated décor throughout. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and steel panel heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Dated sanitary ware throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2 No. Eaton MEM distribution boards in reasonable condition. 1 No. MEM Memshield distribution board at end of lifecycle. | Replace 1 No. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Internal Luminaires | B | 6 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Electrical Systems | Emergency Luminaires | B | 6 |  |  | 0 |  | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Security system in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | H Block | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Structure | Frames | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some spalling and cracking noted to external concrete frame exposing rebar. | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some minor wall damage noted. | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Windows | B | 10 |  |  | 0 |  | UPVC double glazed windows appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No double door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Automatic Doors | B |  |  |  | 0 |  | 1No automatic shutter door within level -1 appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Timber / UPVC Detail | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rotting noted to some external timber panelling and timber facias. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal railings and barriers appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Pitched roof covering appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Roof | Rain Water Goods | B | 6 |  |  | 0 |  | Rainwater goods appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | DHW Storage / Non Storage | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Heatrae Sadia hot water cylinder appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No hot water pumps appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Switchgear | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 2No LV panels within level -1 appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Sub-mains | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Submains appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Carpark surface appears to be aged and at end of recommended design life, including car park bay markings. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Heating Systems | Heat Emitters | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Heating Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Medical gas pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Medical vacuum pump set appears to be aged and approaching end of recommended design life, circa 2008. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | 2No air compressors appear to be in good condition, circa 2018. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall finishes. | Repair wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Ceilings appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No nurse station, 1No staff kitchen & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (fixed units). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Hot & Cold Water Systems | Distribution | B | 8 |  |  | 0 |  | Hot and cold water pipework appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Hot & Cold Water Systems | Insulation | B | 8 |  |  | 0 |  | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some sanitary ware appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 14No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Medical Gas | Distribution | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Some upgrades noted, however the majority of the medical gas system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Medical Gas | Outlets | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Medical Gas | Alarm Systems | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 8 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 10 |  |  | 0 |  | 3No Ariston P.O.U local water heaters appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 76No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 2No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 2No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Wiring Systems - Power | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Power wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Lighting wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Alarms & Detection Systems | Security Systems | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Intruder alarm system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Communication Systems | Telephone/Data Systems | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Telephone/data systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Helen Donald Unit | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some cracking and movement noted to external brick wall to rear elevation. | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Structure | Frames | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steel frame pipework supports within level -1 plant room (-010012) appear to be severely corroded and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor wall damage noted at low level on the north west corner of the building. | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor damage noted to external columns. | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Steel framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | 1No external timber single door appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | B | 6 |  |  | 0 |  | 8No external timber double door sets appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No large external timber double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 3No large external timber double door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external steel and glazed single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 8No external steel and glazed double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No external steel double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Automatic Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No aluminium and glazed single sliding doors appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Automatic Doors | B | 8 |  |  | 0 |  | 2No aluminium and glazed double sliding door sets appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Decoration | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Painted finish to external metal canopy and railings appears to be aged and worn. | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Decoration | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Painted finish to external columns appears to be aged and worn. | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Fabric | Decoration | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Painted finish to 2No external steel double door set appears to be aged and worn. | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some flat roof coverings appear to be aged and at end of recommended design life. (External canopies & internal courtyard roofs). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some flat roof coverings appear to be aged and at end of recommended design life. (Main building external roof walkway). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Paving flags to internal courtyard areas appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | External fire escape staircase appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Gas supply pipework within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No plate heat exchangers within level -1 plant room appear to be aged and at end of recommended design life. (PHE No 1-4 hot water & PHE No 5 heating). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 0 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Controls / Meters | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel within level -1 plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate receiver vessel including pumps and control panel within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 6No belt driven heating pumps within level -1 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  | Water treatment plant & salt saturator within level -1 plant room appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Cold water storage tanks within level 4 appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No sump pump within level -1 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No supply AHUs within level 4 plant rooms appear to be aged and at end of recommended design life. ( South/East, Knutsford Suite, South/West & Delivery Suite). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No supply AHUs within level 4 plant rooms appear to be aged and at end of recommended design life. (General vent No1, General vent No2 & Delivery Suite). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within level 4 plant rooms appears to be aged and at end of recommended design life. (Starfish Ward). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No supply & extract AHUs within level 4 plant rooms appear to be aged and at end of recommended design life. (Gynae Theatre, Gynae Recovery & AHU No3). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 10No belt driven extract fans within level 4 plant rooms appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of ventilation distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 6 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 7 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 8 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 10 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No small refrigeration chiller appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No external Airedale flat bed chillers at roof level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (substation ventilation) within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some mechanical control panels within level 4 plant rooms appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some mechanical control panels within level 4 plant rooms appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Ventilation Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above within ventilation distribution. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Lifts & Hoists | Passenger | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 2No Liftec 26 person 1800kg passenger lifts appear to be aged and approaching end of recommended design life. (Lifts No 12 & 13). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Lifts & Hoists | Passenger | B | 9 |  |  | 0 |  | 2No Liftec 26 person 1950kg passenger lifts appear to be in good condition, however long term replacement will be required.(Lifts No 14 & 15). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No lift control panels appear to be aged and at end of recommended design life. (Lifts No 12, 13, 14 & 15). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No G.U.M clinic changeover switch within level -1 electrical plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level 0 electrical plant room (000098) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level 1 electrical plant room (010097) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level 2 electrical plant room (020104) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No incoming LV panel within level 3 electrical plant room (030122) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Luminaires External | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Luminaires External | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Electrical Systems | Luminaires External | B | 10 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | External Intercom Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external intercom system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | CCTV System | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | UPS / IPS Systems | B |  |  |  | 0 |  | Starkstrom UPS & IPS units within level 0 appear to be in good condition, circa 2021. (Maternity). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | UPS / IPS Systems | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Starkstrom IPS unit within level 2, circa 2011 appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | UPS / IPS Systems | B |  |  |  | 0 |  | Starkstrom IPS units within level 3 appear to be in good condition. (Theatres). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | All | All | Miscellaneous | Fire Suppression System | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No FM200 fire suppression system within level 1 appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceiling tiles appear to be stained and damaged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Ceilings | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Some suspended ceilings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to concrete floors appears to be aged and worn throughout. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Manifolds | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No medical gas manifold appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | Medical vacuum pump set appears to be in good condition, circa 2013, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 2No Atlas Copco receiver vessels appear to be in good condition, circa 2013, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Internal Luminaires | B | 8 |  |  | 0 |  | The majority of internal luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Electrical Systems | Emergency Luminaires | B | 8 |  |  | 0 |  | Emergency luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No Reception desk & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen & 1No reception desk). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No staff kitchen). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Ventilation Systems | Local Extract | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | 1No local extract fan appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Ventilation Systems | Local Extract | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | 1No local extract fan appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No panic alarm system for toilets appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No nurse station & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No nurse station & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No AGSS simplex appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | 1No macerator appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Wiring Systems - Power | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | The majority of power wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | The majority of lighting wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | The majority of emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Communication Systems | Telephone/Data Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some telephone/data systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No staff kitchens & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  | Sanitary ware appears to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No macerator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No nurse stations). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | B |  |  |  | 0 |  | P.O.U local water heaters appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No surgeons panels appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | The majority of emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some nurse call systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Block walls appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Medical Gas | Distribution | B |  |  |  | 0 |  | AGSS pipework appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | 1No duplex AGSS pump set appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 12No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Maternity Block | Level 4 Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | External cladding in a good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Windows | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Timber framed, narrow-gauge double glazed windows are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Doors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Timber external doors are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  | Timber fascias and soffits appear to be in a reasonable condition although redecoration is required (costed elsewhere). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | External redecoration required to timber fascias and soffits. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Roof | Coverings - Pitched | B | 8 |  |  | 0 |  | Pitched roof covering may require lifecycle replacement within the 10 year period. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | uPVC rainwater goods appear to be in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  | No access to inspect (possible local boiler in-situ as flue visible above roof). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External luminaires are aged. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings showing signs of wear and tear. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors appear adequate. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to fixed units. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Decoration | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Internal Fabric & Fixtures | Decoration | B | 9 |  |  | 0 |  | Lifecycle redecoration required. | Redecorate throughout. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Heating Systems | Pipework | B |  |  |  | 0 |  | Radiators and pipework appear to be in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Heating Systems | Heat Emitters | B |  |  |  | 0 |  | Radiators and pipework appear to be in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Foster cold Room and associated equipment is aged and beyond design life. Risk reflects unconfirmed usage requirement at time of survey. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Distribution board is aged and beyond design life. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring is assumed to be aged and due for replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Wiring is assumed to be aged and due for replacement. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | LED fittings. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | No access to inspect panel but field devices where visible, appear in a good condition. | Lifecycle replacement. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | NEQAS | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Mortar missing to some areas of low level brickwork. | Repoint low level brickwork where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Walls & Finishes | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External profile sheet walls to level 3 plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal railings and handrails appears to be aged and worn. | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Profiled sheet pitched roof covering to level 3 plant rooms appears to be aged and at end of recommended design life, evidence of water ingress within plant rooms at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Felt flat roof coverings to main building appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | External fire escape staircase appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No horizontal steam - LTHW calorifiers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Alfa Laval plate heat exchanger for heating appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Controls / Meters | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No mechanical control panel within level -1 external plant room appears to be redundant. | No cost identified. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 0 external plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Controls / Meters | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel within level -1 external plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate receiver vessel including pumps and control panel within level -1 external plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No VT heating pumps within level -1 external plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Water purification plant within level 3 plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | Cold water storage tank within level 3 plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Hot & Cold Water Systems | Pumps | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No sump pump within level -1 external plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No AHU for mortuary within level 0 external plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No belt driven supply fan within level 3 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fume extract fans at roof level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fume extract fans within level 3 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No fume extract fan within level 3 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No Cyclone belt driven extract fans within level 3 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Cyclone belt driven extract fan within level 3 plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Extract Plant | B | 6 |  |  | 0 |  | 2No belt driven extract fans within level 3 plant room appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of ventilation distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | 1No A.C split system appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No COS refrigeration chillers appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No external Airedale flat bed chillers to level 1 flat roof area appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No mechanical control panels within level 3 plant room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Ventilation Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above within ventilation distribution. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Bennie Lifts 2240lbs 12 person passenger lift, circa 1976 appears to be original and due replacement including lift motors and controls. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within lift replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No ICW Power LV incoming panel within level -1 external plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Luminaires External | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Mortuary Refrigerators | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Mortuary refrigerators appear to be aged and at end of recommended design life. Total of 60 body spaces. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Air Tube Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Quirepace air tube terminal within level 2 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Miscellaneous (Block) | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 2No external medical gas manifolds appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | All | All | Miscellaneous | Miscellaneous (Block) | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 1No KAESER air compressor within level -1 external plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | Distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Wiring Systems - Power | B | 6 |  |  | 0 |  | Power wiring appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Wiring Systems - Lighting | B | 6 |  |  | 0 |  | Lighting wiring appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level -1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | Fire alarm system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No intruder alarm system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of fixed furniture appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Medical Gas | Distribution | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Medical gas system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Medical Gas | Outlets | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Medical Gas | Alarm Systems | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Sterilizers | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No LTE Autoclaves appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No cold store appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | Fire alarm system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of fixed furniture appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No fume cupboard appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No cold store appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | B | 10 |  |  | 0 |  | 1No P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | Fire alarm system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B | 10 |  |  | 0 |  | Fire alarm system appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Pathology | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Severe corrosion noted to low level external brick work to all elevations. | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Minor damage noted to external concrete to front elevation exposing rebar. (Front elevation). | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Minor cracking noted to external render. (Front Elevation). | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Walls & Finishes | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Metal profile sheeting panels to external link bridge and roof top plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 8No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 5No external timber double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No external timber double door set appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 2No external timber double door sets appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No aluminium and glazed double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Automatic Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No aluminium and glazed double sliding door set appears to be aged and at end of recommended design life. (CDU entrance). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Automatic Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No aluminium and glazed double sliding door sets appears to be aged and approaching end of recommended design life. (CDU entrance & main entrance). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Automatic Doors | B | 6 |  |  | 0 |  | 1No aluminium and glazed double sliding door set appears to be in good condition, however long term replacement will be required. (South stairwell entrance). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Timber / UPVC Detail | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No external timber panel to link corridor linking the main building to external prefabricated building appears to be aged and rotten. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal railings appears to be aged and worn. (Front elevation). | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal canopies appears to be aged and worn.(Main entrance & CDU entrance). | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to aluminium frames to windows at main entrance appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external disabled access ramp appears to be aged and worn. (Front elevation). | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Painted finish to external render appears to be aged and worn. (Front elevation). | Lifecycle preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal roof edge protection barriers appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some profile sheet pitched roof appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of flat roof coverings to appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Walls | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Corrosion and damage noted to external brick wall to front elevation. | Repair. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External chain-link fencing and gate to ground level appears to be aged and damaged. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  | External fire escape appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No Heat Transfer Ltd Horizontal steam calorifiers within level 1 plant room (010232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 1 plant room (010235) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No BMS outstation control panel within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (Condensate pump) within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within level 1 plant room (010232) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (Fracture clinic) within level 2 plant room (020232) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No mechanical control panels (Comfort controls & MCC-2-3-4)) within level 2 plant room (020232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | B | 10 |  |  | 0 |  | 2No mechanical control panels (Endoscopy & MRI & CP-1-10-3-3) within level 3 plant room (030184) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No BMS outstation control panel within level 7 plant room (070036) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Controls / Meters | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (MCC-02) within level 7 plant room (070005) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate receiver vessel including pumps within level 1 plant room (010232) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No condensate receiver vessel including pumps and controls within level 2 plant room (020232) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No heating pump within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No belt driven heating pumps within level 1 plant room (010232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating Systems | Heating Pumps | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 11No heating pumps within level 1 plant room (010234) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No water treatment plant set within plant room (010236) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  | Water treatment & R/O plant within level 4 courtyard plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No steel cold water storage tank within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Pumps | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No hot water pumps within level 1 plant room (010234) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Pumps | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No hot water pumps within level 1 plant room (010234) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Pumps | B | 8 |  |  | 0 |  | 5No destratification pumps for hot water calorifiers within level 1 plant room (010234) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Pumps | B | 10 |  |  | 0 |  | 2No treated cold water pumps within level 1 plant room (010234) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Hot & Cold Water Systems | Pumps | B | 10 |  |  | 0 |  | 2No untreated cold water pumps within level 1 plant room (010234) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | 1No Ves Andover external box supply fan at ground level appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No inline supply fan within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No supply AHUS (S14, S15, S16, S17 & S18) within level 2 plant room (020232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B | 6 |  |  | 0 |  | 1No Trane supply AHU within level 2 plant room (020232) appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No supply AHUs (S9 & S10) within level 7 plant room (070005) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No supply AHUs (S8, S11 & S12) within level 7 plant room (070005) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No supply AHUs (S5 & S6) within level 7 plant room (070036) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No supply AHUs (S2 & S3) within level 7 plant room (070036) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No Balair external supply & extract AHU (A&E) within level 2 internal courtyard appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 3No external supply AHUs within level 3 internal courtyard appear to be in aged and approaching end of recommended design life.. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B | 8 |  |  | 0 |  | 1No Balair external supply & extract AHU (MRI level2 & endoscopy level3) within level 3 internal courtyard appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply & extract AHU (CCD Intensive Care) within level 7 plant room (070036) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 6No external Balair supply & extract AHUs (Theatres1-5 & Recovery) at roof level appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No external Balair supply & extract AHU (Critical care) at roof level appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 2No external Balair supply AHUs (System 1 ground & AAU No 1) at roof level appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Ventilation Plant | B | 6 |  |  | 0 |  | 1No external supply & extract AHU at level 3 next to link bridge appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No Ves Andover external box extract fan at ground level appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 1No Nuaire external box extract fan at ground level appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No inline extract fan within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 7No Cyclone belt driven extract fans (E16A, E16B, E18A, E18B, E20A, E20B & fracture clinic) within level 2 plant room (020232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No Cyclone belt driven extract fans (E14, E15, E19 & E21) within level 2 plant room (020232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No fume extract fan (E28) within level 2 plant room (020232) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external fume extract fan at level 4 appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 9No Cyclone belt driven extract fans (E9, E10A, E10B, E11, E12A, E12B, E13A, E13B & E30) within level 7 plant room (070005) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No Cyclone belt driven extract fans (E7 & E8) within level 7 plant room (070036) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No Cyclone belt driven extract fans (E4, E5A, E5B,& E6) within level 7 plant room (070036) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external inline extract fan at roof level appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No external fume extract fans at roof level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of ventilation distribution appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some A.C split systems appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 6 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 7 |  |  | 0 |  | 1No A.C split system appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 8 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 9 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 10 |  |  | 0 |  | Some A.C split systems appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No Airdale external A.C condensers at roof level appear to be aged and at end of recommended design life. (System 1 general supply AHU & AHU No1 supply) | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Riedal external chiller at ground level appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No Flowcool external chiller at ground level appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 3No Airedale external flat bed chillers within level 2 internal courtyard appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | B | 10 |  |  | 0 |  | 1No Parker Hiross Hyperchill external chiller within level 2 internal courtyard appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | B | 7 |  |  | 0 |  | 3No Daikin chillers within level 7 plant rooms (07006 & 07005) appear to be in good condition circa 2010, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | B | 7 |  |  | 0 |  | 3No large external flat bed chillers at roof level appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No Airdale external flat bed chillers at roof level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Distribution | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No chilled water dosing pot within internal courtyard appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of chilled water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Buffer Vessels | B |  |  |  | 0 |  | 1No chilled water buffer vessel appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No duplex chilled water pump set within level 3 internal courtyard appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Pumps | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No chilled water pump for external A&E supply and extract AHU within internal level 2 courtyard appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Chilled Water Pumps | B | 7 |  |  | 0 |  | 2No chilled water primary pumps within level 7 plant room (07005) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | 2No external mechanical control panels at ground level appear to be aged and approaching end of recommended design life. (MRI Suite). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (Extract fans) within level 1 plant room (010094) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (substation ventilation) within level 1 switch room (010095) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (Resuscitation AHU) within level 2 plant room (020232) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (Endoscopy AHU) within level 4 external courtyard plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (Water treatment plant) within level 4 external courtyard plant room appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (CP-2-4-8-4)) within level 7 plant room (070005) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (MCC-04) within level 7 plant room (070005) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (CCD Intensive Care) within level 7 plant room (070036) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel (Level 6 CCD) within level 7 plant room (070036) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (MCC-03) within level 7 plant room (070036) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Controls | B(C) | 2 | Possible (3) | Moderate (3) | 9 | Moderate | 1No mechanical control panel (MCC-01) within level 7 plant room (070036) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Ventilation Systems | Insulation | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Cost included above within ventilation distribution. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Lifts & Hoists | Passenger | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No lift car appears to be aged and worn. (Lift No4). | Refurbishment will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Lifts & Hoists | Control Panels | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No lift control panel appears to be aged and at end of recommended design life. (Lift No 7). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  | No access, maintained by RJP Power Networks. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 1 plant room (010234) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 2 plant room (020223) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No MRI changeover switch within level 2 plant room (020223) appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | B | 10 |  |  | 0 |  | 1No LV panel within level 1 switch room (010095) appears to be in good condition, however long term replacement will be required. (Level 1 MCCB Panel board). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No Bypass Panels within level 7 hub room (070027) appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 7 lift motor room (5&6) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No rising busbar systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  | Lightening protection appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of external luminaires at roof level appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external flood lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Electrical Systems | Luminaires External | B | 10 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of the Trend BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Air Tube Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Quirepace air tube terminal unit within A&E appears to be aged and at end of recommended design life. Ductwork, where visible appears to be in reasonably good condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Air Tube Systems | B | 8 |  |  | 0 |  | 1No air tube pump within electrical riser (010026) appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Wet And Dry Risers | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Dry risers appear to be in good condition, however some doors / covers appear to be aged / missing. | Replace aged / missing doors / covers. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | External Intercom Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No external intercom systems appear to be aged and at end of recommended design life. (CDU entrance & north west stairwell). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | CCTV System | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external CCTV cameras appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | UPS / IPS Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No Starkstrom IPS units within level 2 plant room (020232) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | UPS / IPS Systems | B | 8 |  |  | 0 |  | 2No Starkstrom IPS units within level 7 hub room (070027) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | UPS / IPS Systems | B | 8 |  |  | 0 |  | 2No Starkstrom IPS units within level 1 room (010042) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | UPS / IPS Systems | B | 10 |  |  | 0 |  | 4No Starkstrom IPS units & 1No UPS unit within level 3 plant room (030184) appear to be in good condition, however long term replacement will be required. (Endoscopy). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | All | All | Miscellaneous | UPS / IPS Systems | B |  |  |  | 0 |  | Starkstrom IPS & UPS units within level 7 plant room appear to be in good condition. (Theatres1-4). |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | Some floor coverings appear to be in reasonably good condition, however long term replacement will be required. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (2No staff kitchens,1No reception desk & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 4No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Manifolds | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No medical gas manifolds within plant room (010238) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | Medical vacuum pump set and control panel appears to be in good condition, circa 2023. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 4No Atlas Copco medical air compressors within plant room (010235) appear to be in good condition, however long term replacement will be required, circa 2013. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 1No Beacon Medaes dryer unit within plant room (010235) appear to be in good condition, however long term replacement will be required, circa 2013. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 3No medical air & 2No vacuum receiver vessels within plant room (010234) appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 6No macerators appear to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 14No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 4No distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 2No distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No internal local intercom systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Panic alarm system within A&E appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call systems appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No reception desk & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No reception desk). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 1No duplex AGSS pump set appears to be in good condition, however long term replacement will be required. (Endoscopy). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No macerator appears to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 15No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 2No distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (4No nurse stations, 2No staff kitchens, 1No reception desk & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (Fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No nurse station). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 5No macerators appear to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 4No Getinge washer/disinfector units appear to be aged and approaching end of recommended design life. (Endoscopy). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 3No Getinge dryer units appear to be aged and approaching end of recommended design life. (Endoscopy). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 4No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 6No distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | B | 6 |  |  | 0 |  | Some floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No nurse station & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (Fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (3No nurse stations & 1No staff kitchen). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end if recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Ventilation Systems | Local Extract | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | 2No large local extract fans within level 4 external courtyard plant room appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B |  |  |  | 0 |  | 2No ABAC air compressors within level 3 external courtyard plant room appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 5No macerators appear to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 2No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | B | 8 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | Some floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some upgrades noted, however the majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No nurse station & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No staff kitchens). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No staff kitchens). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (5No nurse stations). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 7No macerators appear to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 2No Zip P.O.U local water heaters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 5 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | Some floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (2No staff kitchens & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (3No nurse stations & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of sanitary ware appears to be in good condition, however some appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Ventilation Systems | Local Extract | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Medical Gas | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some of the medical gas system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Medical Gas | Outlets | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Medical Gas | Alarm Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Cost included above within medical gas system replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Bedpan Disposal | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 3No macerators appear to be aged and at end of recommended design life. Frequent breakdowns were reported at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Fixed Plant / Equipment | Miscellaneous | B | 8 |  |  | 0 |  | 1No Zip P.O.U local water heater appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Distribution Boards | B | 6 |  |  | 0 |  | 4No distribution boards appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of nurse call systems appear to be in good condition, however some appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 6 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered ceiling finishes. | Repair plastered ceiling finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No electrical twin tube heaters within lift 5 & 6 motor room appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Distribution | B |  |  |  | 0 |  | AGSS pipework appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 3No duplex AGSS pump sets within level 7 plant room (070005) appear to be in good condition, however long term replacement will be required. (MRI, Theatre3 & 4). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 3No duplex AGSS pump sets within level 7 plant room (070036) appear to be in good condition, however long term replacement will be required. (Procedure room, theatres1 & 2). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | B | 10 |  |  | 0 |  | 1No simplex AGSS pump set within level 7 plant room (070005) appears to be in good condition, however long term replacement will be required. (Phase 2 CED). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No isolator appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some upgrades noted, however the majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Communication Systems | Radio and Television Systems | B |  |  |  | 0 |  | Hospital radio studios were not in use at the time of survey but equipment appeared to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 7 Roof Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of wall panels. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Heating Systems | Pipework | B |  |  |  | 0 |  | Heating pipework appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Heating Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm panels and field devices appear to have been replaced, however the fire alarm wiring appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Princess Michael of Kent | Level 8 Roof Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Windows | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Roof | Coverings - Flat | B | 6 |  |  | 0 |  | Flat roof coverings appear to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Roof | Rain Water Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No A.C split system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Electrical panel heaters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Ventilation Systems | Local Extract | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | 1No local extract fan appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Fixed Plant / Equipment | Miscellaneous | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Zip P.O.U local water heater appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Electrical Systems | Emergency Luminaires | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | PMOK Portacabin | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some cracking and movement noted to external brick walls. | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Mortar missing to some areas of external walls. | Repoint where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber framed single glazed windows appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double glazed window units appear to have blown seals and will require replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4No external timber single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No external timber double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber cladding and facias to roof plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external concrete appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external metal railings appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof coverings to appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof lights appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Boiler Plant | B |  |  |  | 0 |  | 1No Ideal Evomax gas fired boiler appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Pressurisation Plant | B |  |  |  | 0 |  | 1No Boss heating pressurisation unit appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | DHW Storage / Non Storage | B |  |  |  | 0 |  | 1No Megaflo hot water cylinder within level 1 roof plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No water treatment control panel within level 1 roof plant room appears to be redundant. | Replace if required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Controls / Meters | B |  |  |  | 0 |  | 1No small water treatment control panel within level 1 roof plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Heating Systems | Heating Pumps | B | 8 |  |  | 0 |  | 2No VT heating pumps within level 1 roof plant room appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | B |  |  |  | 0 |  | Water treatment plant appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | B |  |  |  | 0 |  | 1No treated water tank within level 1 roof plant room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Hot & Cold Water Systems | Pumps | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Extract Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No A.C split system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Room Split Chillers / Compressors | B | 8 |  |  | 0 |  | 3No A.C split systems appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No LV panel within level 1 roof plant room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | The majority of submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external luminaire appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external luminaires appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Electrical Systems | Luminaires External | B | 8 |  |  | 0 |  | Some external flood lights appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | BMS system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | The majority of double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some fixed furniture appears to be aged and at end of recommended design life. (1No nurse station & fixed units). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Some fixed furniture appears to be aged and approaching end of recommended design life. (1No staff kitchen & fixed units). | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Heating Systems | Pipework | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Heating pipework appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Heating Systems | Heat Emitters | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Some upgrades noted, however the majority of heat emitters appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Heating Systems | Insulation | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Hot & Cold Water Systems | Distribution | B | 6 |  |  | 0 |  | Hot and cold water pipework appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Hot & Cold Water Systems | Insulation | B | 6 |  |  | 0 |  | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B | 8 |  |  | 0 |  | Some sanitary ware appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | B | 6 |  |  | 0 |  | Internal drainage appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 7No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 2No local extract fans appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No distribution boards appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some emergency luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fire alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Intruder alarm system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Panic alarm system for toilets appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Heating Systems | Pipework | B(C) | 1 | Likely (4) | Moderate (3) | 12 | Significant | Heating pipework appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Heating Systems | Insulation | B(C) | 1 | Likely (4) | Insignificant (1) | 4 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Hot & Cold Water Systems | Distribution | B | 6 |  |  | 0 |  | Hot and cold water pipework appears to be in reasonably good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Hot & Cold Water Systems | Insulation | B | 6 |  |  | 0 |  | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 5No isolators appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Distribution Boards | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Renal Unit | Level 1 Roof Plant Rooms | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Structure | Walls | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some areas of spalling concrete and exposed rebar noted at the time of survey | Budget cost allowance for a full structural survey and repair works to be carried out. Note; depending on the outcome of the structural survey further remedial works may be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some aluminium framed single glazed windows to level 0 appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Doors | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | 3No external timber single door appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No external timber double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No aluminium and glazed double door set appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Automatic Doors | B(C) | 1 | Likely (4) | Minor (2) | 8 | Moderate | 2No aluminium and glazed double door sets with automatic openers appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Painted finish to external concrete window lintels appears to be aged and worn. | Preparation and redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Flat roof coverings to appear to be aged and at end of recommended design life. Patch repairs noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Roof | Roof Lights | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internally fixed rain water goods appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No horizontal steam calorifiers for heating within plant room (000038) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2No vertical steam calorifiers for hot water within plant room (000038)appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Controls / Meters | B | 7 |  |  | 0 |  | 1No mechanical control panel within plant room (000038) appears to be aged in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Steam and Condensate | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Steam and condensate pipework within plant room (000038) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Energy Centre Systems | Steam and Condensate | B |  |  |  | 0 |  | 1No condensate receiver vessel & pump set appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No belt driven CT pumps within plant room (000038) appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No duplex VT pump set within plant room (000038) appears to be aged and at end of recommended design life. (Zone1). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No duplex VT pump set within plant room (000038) appears to be aged and at end of recommended design life. (Zone2). | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No small destratification pump within plant room (000038) appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No supply AHU within roof plant room (030002) appears to be redundant. | Budget cost included if replacement is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 3No belt driven extract fans within roof plant room (030002) appear to be redundant. | Budget cost included if replacement is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  | Note; new ventilation system & controls being installed at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 6No A.C split systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Controls | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No mechanical control panel within roof plant room (030002) appears to be redundant. | Budget cost included if replacement is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Controls | B |  |  |  | 0 |  | Note; new ventilation system & controls being installed at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  | Note; new ventilation system & controls being installed at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 2No Liftec 26 person 2000kg passenger lifts appear to be in good condition including lift motors and control panels, modernised in 2017. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No isolators within roof plant room (030002) appear to be aged and at end if recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some submains appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Lightning Protection | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Lightening protection appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some external luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Electrical Systems | Luminaires External | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some external luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Communication Systems | Building Management systems | B |  |  |  | 0 |  | Note; new ventilation system & controls being installed at the time of survey. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Air Tube Systems | B |  |  |  | 0 |  | Quirepace air tube terminal appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | CCTV System | B |  |  |  | 0 |  | External CCTV cameras appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | All | All | Miscellaneous | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some suspended ceilings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some floor coverings appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Some floor coverings appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | The majority of floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B | 10 |  |  | 0 |  | Some fixed furniture appears to be in good condition, however long term replacement will be required. (1No reception desk). | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Some sanitary ware appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No local extract fan appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Ventilation Systems | Local Extract | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | 1No local extract fan appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Ventilation Systems | Local Extract | B | 8 |  |  | 0 |  | 1No local extract fan appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Medical Gas | Distribution | B |  |  |  | 0 |  | Medical gas system appears to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Medical Gas | Outlets | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | B(C) | 5 | Possible (3) | Insignificant (1) | 3 | Low | 2No macerators appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B |  |  |  | 0 |  | P.O.U local water heaters appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Distribution Boards | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 1No distribution board appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some power wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some lighting wiring appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some internal luminaires appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Internal Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some internal luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Electrical Systems | Emergency Luminaires | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | Some emergency luminaires appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No intercom system appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original analogue telephone system and some original data systems appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Wandsworth nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Damage noted to some areas of plastered wall finishes. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B | 8 |  |  | 0 |  | The majority of floor coverings appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some single doors appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some double door sets appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | The majority of internal decorations appear to be aged and at end of recommended design life. | Redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Long term redecoration will be required. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heat emitters appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water pipework appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Cost included above within pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  | Sanitary ware appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Medical Gas | Distribution | B |  |  |  | 0 |  | Medical gas system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Medical Gas | Outlets | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Medical Gas | Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | B(C) | 5 | Possible (3) | Minor (2) | 6 | Low | 1No Zip P.O.U local water heater appears to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Distribution Boards | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | 2No distribution boards appear to be aged and approaching end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  | Power wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Internal luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  | Emergency luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  | Fire alarm system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | Secure door system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Wandsworth nurse call system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | N/A |  |  |  | 0 |  | No access to level 2 at the time of survey due to building works. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Ceilings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1No distribution board within roof lift motor room appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring to roof plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Lighting wiring to roof plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal luminaires to roof plant rooms appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Emergency luminaires to roof plant rooms appear to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fire alarm system to roof plant rooms appears to be aged and at end of recommended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Shrodells Building | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | Appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Original timber windows are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Windows | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Powder coated windows appear to be aged and are nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Double timber door sets are aged and in poor condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Automatic Doors | B(C) | 3 | Possible (3) | Moderate (3) | 9 | Moderate | Automatic entrance doors are aged and nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Roof | Coverings - Flat | B |  |  |  | 0 |  | Flat roof covering appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Roof | Roof Lights | B |  |  |  | 0 |  | Polydome roof lights appear to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Rainwater goods appear to be aged and are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | External Building Works | Fire Escapes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Controls / Meters | Dx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1N medium size control panel to roof level plant room appears to be aged and possibly redundant. | Replace / remove as required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No water tank circa 1981 is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Large Kitchen supply fan is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Ventilation Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Dining Servery supply fan is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Dining Servery extract fan is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No aged toilet extract fans are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No Large kitchen extract fan is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Distribution | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged ventilation ductwork noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Chillers / Cooling Systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 4No refrigeration chillers located externally are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Lifts & Hoists | Goods | B | 8 |  |  | 0 |  | 4No kitchen lifts serving two floors are in reasonable condition. | Long term replacement is anticipated. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | MEM LV Switchboard appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  | Appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Electrical Systems | Luminaires External | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | Wear and tear evident to external lighting system. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Communication Systems | Building Management systems | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | BMS System appears to be aged and in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Ceilings | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Some suspended ceilings appear to be aged and are nearing end of design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to some internal floor coverings. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Many internal single doors appear to be aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Many internal double doors appear to be aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to internal décor. | Internal redecoration is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Minimal defects noted. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating system appears to be aged and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and are due replacement | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Aged hot and cold water infrastructure noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged sanitary ware noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged internal drainage system noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Wiring Systems - Power | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of some local replacement, however, some original systems remain in situ. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Wiring Systems - Lighting | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of some local replacement, however, some original systems remain in situ. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Internal Luminaires | B(C) | 3 | Possible (3) | Minor (2) | 6 | Low | Majority of internal light fittings have been replaced with LED, however, some aged fittings remain. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Telecommunication systems appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 3 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to some internal floor coverings. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some internal single doors appear to be aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some internal double doors appear to be aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Wear and tear evident to internal décor. | Internal redecoration is required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Minimal defects noted. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating system appears to be aged and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and are due replacement | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Aged hot and cold water infrastructure noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Aged sanitary ware noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged internal drainage system noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Communication Systems | Telephone/Data Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Telecommunication systems appear to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | First | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Floor Coverings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heating system appears to be aged and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Alarms & Detection Systems | Security Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Spice of Life | Roof Plant Room | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Structure | Frames | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Original timber framed single glazed sash windows are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber doors are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Timber / UPVC Detail | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Paintwork to timber fascia's and soffits in reasonable condition. | Repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Pitched roof coverings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Roof | Coverings - Flat | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  | PVCu rainwater goods in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Boiler Plant | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 3 No. Hamworthy Purewell Variheat Mk2 gas fired boilers at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1 No. calorifier appears to be at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Flues - Separate | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Controls / Meters | B |  |  |  | 0 |  | 1 No. plant room control panel in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Heating Systems | Heating Pumps | B | 8 |  |  | 0 |  | 3 No. Grundfos shunt & 1 No. Grundfos VT pumps in good condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Hot & Cold Water Systems | Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. Grundfos primary, 1 No. Grundfos secondary & 1 No. destratification DHW pumps at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Extract Plant | B |  |  |  | 0 |  | 1 No. flue dilution fan in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Room Split Chillers / Compressors | B(C) | 4 | Possible (3) | Minor (2) | 6 | Low | 1 No. Mitsubishi split air condensing unit in serviceable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Lifts & Hoists | Goods | B | 6 |  |  | 0 |  | 1 No. dumbwaiter 300 kg lift in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  | Lighting protection in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  | External bulkhead light fittings in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Communication Systems | Building Management systems | B |  |  |  | 0 |  | 1 No. Trend BMS outstation in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Fixed units in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and steel panel heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 3 No. Schneider distribution boards in good condition. 1 No. Crabtree distribution board to plant room appears redundant. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Internal Luminaires | B | 8 |  |  | 0 |  | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Communication Systems | Nurse Call Systems | B |  |  |  | 0 |  | Nurse call system in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Internal doors in reasonable condition however nearing end of lifecycle. | Replace 35 No. single & 4 No. double doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 6 |  |  | 0 |  | Fixed kitchen units in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and steel panel heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Schneider distribution board in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Doors | B(C) | 2 | Possible (3) | Minor (2) | 6 | Low | Internal doors in reasonable condition however nearing end of lifecycle. | Replace 30 No. single doors. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B | 6 |  |  | 0 |  | Fixed kitchen units in reasonable condition. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and steel panel heat emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Schneider distribution board in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Internal Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Light fittings in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Sycamore House | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | External walls and cladding appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Windows | B |  |  |  | 0 |  | Aluminium framed double glazed windows appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Doors | B |  |  |  | 0 |  | External doors appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Automatic Doors | B | 10 |  |  | 0 |  | Aluminium and glazed double automatic sliding door sets appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Automatic Doors | B |  |  |  | 0 |  | Automatic roof hatches appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Fabric | Decoration | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  | Profile sheet pitched roof coverings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Roof | Coverings - Flat | B |  |  |  | 0 |  | Felt flat roof coverings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site Physical Condition Report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Extract Plant | B |  |  |  | 0 |  | Smoke vents appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Room Split Chillers / Compressors | B |  |  |  | 0 |  | Mitsubishi A/C split system for UPS battery room appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Controls | B |  |  |  | 0 |  | Smoke vent controls appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  | 3No Kone 1150KG 15 person passenger lifts appear to be in good condition, circa 2021. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  | Lift controls appear to be in good condition, circa 2021. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  | ISS main incoming LV panel appears to be in good condition, circa 2021. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  | External luminaires appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Wet And Dry Risers | B |  |  |  | 0 |  | Dry risers appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Miscellaneous (Block) | B |  |  |  | 0 |  | Inertech SS fire suppressant system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Miscellaneous (Block) | B |  |  |  | 0 |  | Siel UPS system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Miscellaneous (Block) | B |  |  |  | 0 |  | Electrical car chargers appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Miscellaneous (Block) | B |  |  |  | 0 |  | Photovoltaics system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | All | All | Miscellaneous | Miscellaneous (Block) | B |  |  |  | 0 |  | Car park barriers appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Minor damage noted to plastered wall finishes within parking hub. | Repair plastered wall finishes prior to redecoration. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Carpet floor coverings within parking hub are stained and starting to wear due to heavy use. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  | Parking hub staff kitchen appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Decoration | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Internal decoration within parking hub appears to be aged and approaching end of recommended design life. | Lifecycle redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 9 |  |  | 0 |  | Long term redecoration will be required within parking hub. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Heating Systems | Heat Emitters | B |  |  |  | 0 |  | Electrical panel heaters within parking hub appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Ventilation Systems | Local Extract | B | 10 |  |  | 0 |  | Nuaire local extract fans within parking hub appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | B | 10 |  |  | 0 |  | 2No P.O.U local water heaters appear to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Wheelchair refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 0 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 4 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 5 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  | Floor coverings to stairwell areas, carpark surfaces and markings appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Doors appear to be in good condition throughout. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Internal Fabric & Fixtures | Unit Furniture | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Internal Fabric & Fixtures | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Hot & Cold Water Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Hot & Cold Water Systems | Internal Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | Schneider distribution boards appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | LED lighting appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Electrical Systems | Emergency Luminaires | B | 10 |  |  | 0 |  | Emergency lighting appears to be in good condition, however long term replacement will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Alarms & Detection Systems | Fire Alarm System | B | 8 |  |  | 0 |  | Fire alarm system appears to be in good condition, however the long term replacement of control panels and field devices will be required. | Long term replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  | CCTV system appears to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  | Refuge point systems appear to be in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Watford Riverwell Multistorey Carpark | Level 6 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Structure | Frames | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  | Hanging tile finish and brickwork generally in a reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | PVCu frame double glazed windows to front and rear elevations in reasonable condition however single glazed timber frame windows to both side elevations are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber doors are in poor condition. Heavily worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Automatic Doors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Timber / UPVC Detail | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Fabric | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Flaking paintwork to steel fire escape hand rails. | Repaint. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Roof | Coverings - Pitched | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | No access to flat roof areas however flat roof coverings assumed dated from ground level observation. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Roof | Roof Lights | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Single glazed roof lights are heavily worn with some leaks evident to surrounding internal areas at Level 3 stairwell. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Drainage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Roads / Car Parks | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Paths | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Fencing / Gates | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  | Refer to site physical condition report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 2 No. shell & tube calorifiers are heavily dated and past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | DHW Storage / Non Storage | B |  |  |  | 0 |  | Local domestic hot water heaters to each floor level - no direct access to inspect but no major issues noted. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Controls / Meters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1 No. plant room control panel past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Heating Systems | Heating Pumps | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 4 No. Lowara heating pumps at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Hot & Cold Water Systems | Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2No. Roof mounted extract fans are assumed to be aged and due for lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Room Split Chillers / Compressors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 1No. Split air condensing unit to roof (no access to inspect) is assumed to be nearing end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Lifts & Hoists | Passenger | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Passenger lift is original and well beyond intended design life. Lift was out of order at time of survey and looked to have been disused for some time. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | 2 No. Bill fused switch to ground floor plant rooms at end of design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Electrical Systems | Sub-mains | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External bulkhead light fittings are dated and weathered. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Communication Systems | Building Management systems | B |  |  |  | 0 |  | Trend BMS outstation in good condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | All | All | Miscellaneous | Miscellaneous (Block) | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | 1 No. Spirax Sarco condensate recovery unit past intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Ceilings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Majority of suspended ceilings in reasonable condition however sporadic areas of stained tiles throughout. | Replace stained tiles. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Fixed kitchen units are worn and dated. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron emitters in reasonable condition however dated. Small number of steel panel emitters in reasonable condition. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Hager, 1 No. Eaton MEMSHIELD 3, and 2 No. Merlin Gerin distribution boards in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Light fittings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 0 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Unit Furniture | B | 8 |  |  | 0 |  | Fixed kitchen units in reasonable condition. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Merlin Gerin distribution board in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Light fittings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 1 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed kitchen units in reasonable condition. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Merlin Gerin distribution board in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Light fittings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 2 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Moderate (3) | 15 | Significant | Evidence of historic or potentially ongoing water ingress to stairwell plaster ceiling below flat roof. | Further investigation will be required. Budget cost for investigation & remedials. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Floor coverings throughout are worn and dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  | Internal doors in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Unit Furniture | B(C) | 4 | Possible (3) | Insignificant (1) | 3 | Low | Fixed kitchen units in reasonable condition. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Decoration | C | 0 | Certain (5) | Insignificant (1) | 5 | Low | Décor throughout is drab and dated. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Internal Fabric & Fixtures | Decoration | B | 7 |  |  | 0 |  | Lifecycle redecoration. | Redecorate. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework and cast iron emitters in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  | See pipework. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot & cold water distribution in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Hot & Cold Water Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal drainage in reasonable condition however dated. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Ventilation Systems | Local Extract | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | Local extract fans throughout are dated. Lifecycle replacement. | Replace. Budget cost given. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  | 1 No. Merlin Gerin distribution board in serviceable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Power wiring of mixed ages throughout. | Rewire. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  | Lighting wiring in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  | Light fittings in reasonable condition. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Electrical Systems | Emergency Luminaires | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Emergency lighting in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Alarms & Detection Systems | Fire Alarm System | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Fire alarm system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Alarms & Detection Systems | Security Systems | B(C) | 4 | Possible (3) | Moderate (3) | 9 | Moderate | Security system in reasonable condition. Lifecycle replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Alarms & Detection Systems | Other Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Watford General Hospital | Willow House | Level 3 | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Walls & Finishes | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Decayed mortar joints noted to some areas at low level. | Re-point external walls where required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Windows | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Timber windows appear to be aged, in poor condition, and remain in situ beyond intended design life. | Replace aged windows. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External single timber doors are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Doors | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External double timber doors are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Automatic Doors | B(C) | 5 | Possible (3) | Moderate (3) | 9 | Moderate | Auto entrance doors appear to be aged and are nearing end of recommended design life. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Timber / UPVC Detail | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External timber cladding is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Roof | Coverings - Pitched | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Pitch glazed roof lights appears to be aged and remain in situ beyond intended design life. Water ingress noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Roof | Coverings - Flat | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Flat roof covering is aged and noted to be in poor condition. Internal water ingress noted in multiple places at the time of survey. | Replace flat roof covering. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Roof | Roof Lights | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Roof | Rain Water Goods | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Rainwater goods are aged and due replacement. | Replace internally fitted rainwater goods. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Roads / Car Parks | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Paths | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Entrance gates are aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Fencing / Gates | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Timber perimeter fencing is aged and damaged in places. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Boiler Plant | B |  |  |  | 0 |  | 2No Keston gas fired boilers circa 2023. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B |  |  |  | 0 |  | Circa 2023 minimal defects. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Controls / Meters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Heating Systems | Heating Pumps | B |  |  |  | 0 |  | Circa 2023 minimal defects. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Hot & Cold Water Systems | Pumps | B |  |  |  | 0 |  | Circa 2023 minimal defects. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Ventilation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Extract Plant | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Aged toilet extract system noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Room Split Chillers / Compressors | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Chillers / Cooling Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Controls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Ventilation Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Lifts & Hoists | Passenger | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Lifts & Hoists | Control Panels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Electrical Systems | Switchgear | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Main incoming LV panel is aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Electrical Systems | Sub-mains | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Electrical LV Sub mains appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Electrical Systems | Lightning Protection | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Electrical Systems | Luminaires External | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | External lighting system appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Communication Systems | Building Management systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  | Predominantly exposed block work and appears to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Ceilings | C | 0 | Certain (5) | Minor (2) | 10 | Moderate | Soma areas of damaged plasterboard ceiling noted at the time of survey. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  | Suspended ceilings appear to be in good order. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Floor Coverings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Majority of internal floor coverings are aged and worn. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal single doors, many of which are fire doors, appear to be aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Doors | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Internal double doors, many of which are fire doors, appear to be aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Unit Furniture | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | 1No fitted kitchen to staff room is aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Decoration | B(C) | 2 | Possible (3) | Insignificant (1) | 3 | Low | Wear and tear evident to internal décor. | Internal redecoration will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Internal Fabric & Fixtures | Decoration | B | 9 |  |  | 0 |  | Minimal defects noted to internal décor. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Heating Systems | Pipework | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Heating pipework appears to be aged and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Heating Systems | Heat Emitters | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Heat emitters appear to be aged and are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Heating Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Hot & Cold Water Systems | Distribution | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Hot and cold water system appears to be aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Hot & Cold Water Systems | Insulation | Cx | 0 | Certain (5) | Insignificant (1) | 5 | Low | NOTE: Cost included above as part of pipework replacement. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Sanitary ware appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Hot & Cold Water Systems | Internal Drainage | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Internal drainage system appears to be aged and is due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Switchgear | N/A |  |  |  | 0 |  | Refer to block report. |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Distribution Boards | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Memshield 2 distribution boards appear to be aged and remain in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Wiring Systems - Power | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Majority of power circuits appears to be aged and original. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Wiring Systems - Lighting | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Majority of lighting circuits appears to be aged and original. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Internal Luminaires | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Some LED fittings note, however, majority of light fittings appear to be aged and are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Electrical Systems | Emergency Luminaires | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Some LED fittings note, however, majority of emergency light fittings appear to be aged and are due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Alarms & Detection Systems | Fire Alarm System | Cx | 0 | Certain (5) | Moderate (3) | 15 | Significant | Fire alarm system appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Alarms & Detection Systems | Security Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Intruder alarm system is aged and remains in situ beyond intended design life. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Communication Systems | Telephone/Data Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Communication Systems | Nurse Call Systems | Cx | 0 | Certain (5) | Minor (2) | 10 | Moderate | Nurse call system appears to be aged and due replacement. | Replace. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Jacketts Field | Jacketts Field | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Structure | Foundations | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Structure | Walls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Structure | Frames | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Structure | Floors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Structure | Roofs | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Windows | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Automatic Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Timber / UPVC Detail | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Fabric | Decoration | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Roof | Coverings - Pitched | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Roof | Coverings - Flat | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Roof | Roof Lights | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Roof | Rain Water Goods | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Roads / Car Parks | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Paths | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Block / Paved Areas / Tarmac Areas / Concrete Areas | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Walls | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Fencing / Gates | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | External Building Works | Fire Escapes | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Fuel Supply, Storage & Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Boiler Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Pressurisation Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Boiler Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Calorifiers / Heat Exchangers | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | DHW Storage / Non Storage | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Flues - Separate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Controls / Meters | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Generators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Ground/Air source heat pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Energy Centre Systems | Steam and Condensate | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Heating Systems | Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Heating Systems | Heating Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Heating / Hot & Cold Water Systems | General Header Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Heating / Hot & Cold Water Systems | Water Treatment Plant | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Hot & Cold Water Systems | Potable Cold Water Tanks | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Hot & Cold Water Systems | Pumps | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Ventilation Plant | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Extract Plant | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Room Split Chillers / Compressors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Chillers / Cooling Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Chilled Water Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Chilled Water Buffer Vessels | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Chilled Water Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Controls | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Ventilation Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Lifts & Hoists | Passenger | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Lifts & Hoists | Goods | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Lifts & Hoists | Hoists | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Lifts & Hoists | Control Panels | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Electrical Systems | Substations / Transformers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Electrical Systems | Sub-mains | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Electrical Systems | Lightning Protection | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Electrical Systems | Luminaires External | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Communication Systems | Building Management systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Mortuary Refrigerators | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Air Tube Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Industrial Gas Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Wet And Dry Risers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Hydrotherapy Pool | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | All | All | Miscellaneous | Miscellaneous (Block) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Internal Fabric & Fixtures | Decoration | B | 6 |  |  | 0 |  | Minimal defects noted to internal décor. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | Ground | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Walls & Finishes | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Ceilings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Floor Coverings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Doors | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Unit Furniture | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Internal Fabric & Fixtures | Decoration | B | 6 |  |  | 0 |  | Minimal defects noted to internal décor. | Lifecycle replacement will be required. | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Heating Systems | Pipework | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Heating Systems | Heat Emitters | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Heating Systems | Insulation | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Hot & Cold Water Systems | Distribution | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Hot & Cold Water Systems | Insulation | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Hot & Cold Water Systems | Sanitary Ware & Fittings | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Hot & Cold Water Systems | Internal Drainage | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Ventilation Systems | Local Extract | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Medical Gas | Distribution | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Medical Gas | Manifolds | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Medical Gas | Outlets | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Medical Gas | Alarm Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Medical Gas | Medical Air Compressors / Vacuum Pumps | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Sterilizers | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Bedpan Disposal | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Disinfection Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Catering Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Laundry Equipment | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Fixed Plant / Equipment | Miscellaneous | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Switchgear | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Distribution Boards | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Wiring Systems - Power | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Wiring Systems - Lighting | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Internal Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Electrical Systems | Emergency Luminaires | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Alarms & Detection Systems | Fire Alarm System | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Alarms & Detection Systems | Security Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Alarms & Detection Systems | Other Alarm Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Communication Systems | Telephone/Data Systems | B |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Communication Systems | Paging Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Communication Systems | Nurse Call Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Communication Systems | Radio and Television Systems | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
Maple House | Maple House | First | All | Miscellaneous | Miscellaneous (Room) | N/A |  |  |  | 0 |  |  |  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED
[15 empty] | Total Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | Filter Total Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## User notes
1 | The physical condition of each sub-element is categorised as follows:
| A |  | As new and can be expected to perform adequately to its full normal life
| B |  | Sound, operationally safe and exhibits only minor deterioration
| B(C) |  | Currently as B, but will fall below B within five years
| C |  | Operational, but major repair or replacements is currently needed to bring up to condition B
| D |  | Operationally unsound and in imminent danger of breakdown
| X |  | Supplementary rating added to C or D to indicate that it is impossible to improve without replacements
| N/A |  | Not Applicable
2 | Risk Assessment using 5 x 5 matrix categories as below:
| Low Risk: |  | Should be addressed through agreed maintenance programmes or included in the later years of the estate improvement strategy
| Moderate Risk: |  | Should be addressed by close control and monitoring; can be effectively managed in the medium term so as not to cause undue concern to statutory enforcement bodies or risk to healthcare delivery or safety. These items require expenditure planning for the medium term.
| Significant Risk: |  | Require expenditure in the short term but should be effectively managed as a priority so as not to cause undue concern to statutory enforcement bodies or risk to healthcare delivery or safety.
| High Risk: |  | Must be addressed as an urgent priority in order to prevent catastrophic failure, major disruption to clinical services or deficiencies in safety liable to cause serious injury and/or prosecution.
| Risk Ranking |  |  |  | Score Range
| Low |  |  |  | 1-6
| Moderate |  |  |  | 7-10
| Significant |  |  |  | 11-16
| High |  |  |  | 17 - 25
3 | Costs for any Statutory Non-Compliance deemed to be backlog. Each sub-element is ranked according to compliance with mandatory requirements (including 'Firecode') and statutory safety legislation as follows-
| A |  | Complies fully with current mandatory fire safety requirements and statutory safety legislation
| B |  | Complies with all necessary mandatory fire safety requirements and statutory safety legislation with minor deviations of a non-serious nature
| B(C) |  | Currently as B, but will fall below B within five years as a consequence of unabated deterioration or knowledge of impending mandatory fire safety requirements or statutory safety legislation
| C |  | Contravention of one or more mandatory fire safety requirements and statutory safety legislation, which falls short of B
| D |  | Dangerously below conditions A and B
4 | Functional Suitability - Assessed on the basis of three main elements; Internal Space Relationships, Support Facilities and Location
| A | Very satisfactory, no change needed
| B | Satisfactory, minor change needed
| C | Not satisfactory, major change needed
| D | Unacceptable in its present condition
| X | Supplementary rating added to C or D to indicate that nothing but a total rebuild or relocation will suffice (that is, improvements are either impractical or too expensive to be tenable)
5 | Space Utilisation - An overall judgement about Space Utilisation categorised as follows -
| Empty: (E) |  | Empty or grossly under-used at all times (excluding temporary closure)
| Under-Used: (U) |  | Generally under-used, utilisation could be significantly increased
| Fully Used: (F) |  | A satisfactory level of utilisation
| Overcrowded: (O) |  | Overcrowded, overloaded and facilities generally over-stretched
6 | Quality - Each element is assessed to produce an overall ranking of the quality of the estate as follows -
| A |  | Facility of excellent quality
| B |  | A facility requiring general maintenance investment only
| C |  | A less than acceptable facility requiring capital investment
| D |  | A very poor facility requiring significant capital investment or replacement
| X |  | Supplementary rating added to C or D to indicate that nothing but a total rebuild or relocation will suffice (that is, improvements are either impractical or too expensive to be tenable)
7 | Energy - For Strategic Planning Purposes, the ranking for the site and/or building based on the following energy usage per unit volume figures
| A |  |  | 35-55 GJ per 100 cubic metres
| B |  |  | 56-65 GJ per 100 cubic metres
| C |  |  | 66-75 GJ per 100 cubic metres
| D |  |  | 76-100 GJ per 100 cubic metres
| X |  |  | Supplementary rating added to C or D to indicate that nothing but a total rebuild or relocation will suffice (that is, improvements are either impractical or too expensive to be tenable)
8 | Projected Costs - all costs recorded within the reports are net costs only and do not include for on-costs such as contingencies, preliminaries, project management, asbestos removal and VAT etc; an uplift will need to be applied to cover these costs.

## BACK (hidden)
CONDITION |  |  | STATUTORY | FUNCTIONAL |  | SPACE | QUALITY |  | Environment
Condition | REM | Reference | Condition | Condition | Score | Condition | Condition | Score | Condition | Score | Unit | RISK SCORE | RISK | CONSEQUENCE |  | LIKELIHOOD
A | 0 | CONGOOD | A | A | 10 | O | A | 10 | A | 10 | No. | 1 | Low | Catastrophic (5) | 5 | Certain (5) | 5
B | 1 | CONGOOD | B | B | 8 | F | B | 8 | B | 8 | m² | 2 | Low | Major (4) | 4 | Likely (4) | 4
B(C) | 2 | CONPROJ | C | B(C) | 6 | E | B(C) | 6 | C | 6 | m | 3 | Low | Moderate (3) | 3 | Possible (3) | 3
C | 3 | CONIMME | D | C | 5 | U | C | 5 | D | 3 | set | 4 | Low | Minor (2) | 2 | Unlikely (2) | 2
Cx | 4 | CONIMME | N/A | Cx | 4 | N/A | Cx | 4 | N/A |  | task | 5 | Low | Insignificant (1) | 1 | Rare (1) | 1
D | 5 | CONIMME |  | D | 3 |  | D | 3 |  |  |  | 6 | Low
Dx | 6 | CONIMME |  | Dx |  |  | Dx |  |  |  |  | 8 | Moderate
N/A | 7 | CONN |  | N/A |  |  | N/A |  |  |  |  | 9 | Moderate
| 8 | [10 empty] | 10 | Moderate
| 9 | [10 empty] | 12 | Significant
| 10 | [10 empty] | 15 | Significant
CONGOOD | CONPROJ | CONIMME | [9 empty] | 16 | Significant
6 | 1 | 0 | [9 empty] | 20 | High
7 | 2 | [10 empty] | 25 | High
8 | 3
9 | 4
10 | 5
11
12
13
14
15
16
17
18
19
20